| Sl. No. | Clause/ Drg. No. | Existing provision | Amended provision |
| --- | --- | --- | --- |
| 1) | 9.0 Specific Requirements of section Project | 9.0 Specific Requirements 9.1. Relevant / applicable clauses of Specific Requirements as mentioned at CC/ENGG/SECPROJECT/SPECIFIC REQUIREMENT Rev 06 (Attached as Annexure II) shall be referred for specific scope of work. | 9.0 Specific Requirement --- --- 9.1 - Modified as below. Relevant / applicable clauses of Specific Requirements as mentioned at CC/ENGG//SPEC/SECPROJECT/SPECIFIC REQUIREMENT Rev 07 (Attached as Annexure VI) shall be referred for specific scope of work. The requirements pertaining to present scope of work only be applicable. Clause No. 9.2 to 9.7-----Deleted Clause No. 10 -----Deleted |
| 2) | Clause No. 9.2 of Section GTR rev 15 | Clause No. 9.2 of Section GTR rev 15 is amended | The reports for all type tests as per technical specification shall be furnished by the Contractor along with equipment / material drawings. However, type test reports of similar equipments/ material already accepted in POWERGRID shall be applicable for all projects with similar requirement. The type tests conducted earlier should have either been conducted in accredited laboratory (accredited based on ISO / IEC Guide 25 / 17025 or EN 45001 by the national accreditation body of the country where laboratory is located) or witnessed by POWERGRID/representative authorized by POWERGRID/representative of Utility /representative of accredited test lab/ representative of The National Accreditation Board for Certification Bodies (NABCB) certified agency shall also be acceptable. Unless otherwise specified elsewhere, the type test reports submitted shall be of the tests conducted within the years specified below from the date of NOA. In case the test reports are of the test conducted earlier than the years specified below from the date of NOA, the contractor shall repeat these test(s) at no extra cost to the Employer :- S. No.; Name of Equipment; Validity of type test (in years). 1; Power Transformer; 5. 2; LT Transformer; 5. 3; Shunt Reactor; 5. 4; OLTC; 10. 5; Bushing of Power Transformers/Reactors; 7. 6; Fittings and accessories for Power transformers & Reactors; 10. 7; Circuit Breaker; 10. 8; Isolator; 10. 9; Lighting Arrester; 10. 10; Wave Trap; 10. 11; Instrument transformer; 10. 12; GIS & Hybrid GIS; 15. 13; LT Switchgear; 10. 14; Cable and associated accessories; 10. 15; Relays; 7. 16; Capacitors; 10. 17; Battery and Battery charger; 10. 18; Conductor & Earth wire; 10. 19; Insulators ( Porcelain/Glass); 10. 20; Composite Insulators; 5. 21; PLCC; 5. Note For all other equipment’s validity of type test shall be 10 years from date of NOA Further, in the event of any discrepancy in the test reports i.e. any test report not acceptable due to any design/manufacturing changes or due to non-compliance with the requirement stipulated in the Technical Specification or any/all type tests not carried out, same shall be carried out without any additional cost implication to the Employer. The Contractor shall intimate the Employer the detailed program about the type tests at least two (2) weeks in advance in case of domestic supplies & six (6) weeks in advance in case of foreign supplies. |