| Sl. No. | Clause ref. | Existing Provision of the Bidding Document | Query asked by the bidders | POWERGRID’s Clarification |
| --- | --- | --- | --- | --- |
| 1 |  |  | SL.NO; ITEM; Description; UNIT; AS PER PGCIL TECHNICAL SPECIFICATION (Section-VIII- Annexure-B); AS PER BOQ. 1; COMPOSITE LONGROD INSULATOR - 220KV - 120KN; Nominal length; mm; 2030; 2175. 2; COMPOSITE LONGROD INSULATOR - 220KV - 160KN; Nominal length; mm; 2210; 2550. Kindly confirm the same. | As per Clause 4.2, Section IA, TS, Provisions of Section IA shall prevail over other section of TS. Accordingly, length of composite long rod insulators specified under Section-I of Technical Specification shall be adopted for the subject package. BOQ items for CLR Insulator (120KN & 160KN) has been modified accordingly. Refer Amendment no. 1 in this regard. |