| Clarification - 3 dated: xx/xx/xx22 to Bidding Document for Transmission line package TL01 for construction of 220 kV D/C (Twin Moose) Transmission Line from 120 MW Rangit IV HEP to New Melli Pooling Station (POWERGRID) & associated Bays at New Melli GIS S/S associated with consultancy services to JPCL (a fully owned subsidiary of NHPC). Specification No - 5002002309/CONSULTANCY GIVEN/DOM/A04-CC CS -5 |  |  |  |
| --- | --- | --- | --- |
| Sl. No. | Reference Document | Query asked by the bidders | POWERGRID reply |
|  | Clause no / Page no |  |  |
| 1 | Section Project- Cl No. 2.2.1.1 -II (c ) | As per referred Cl no. If required hardware to be upgraded for SAS. Please specify the exact requirement or arrange to provide the existing SAS hardware details including version for checking upgradation requirement because during site visit same can't be identified. | Requirement is ample clear in bidding document, provided with typical architecture. Present scope includes augmentation of existing substation automation system (Alstom make), based on IEC 61850, Bidders to assess the hardware requirement for the bays under present scope & the same shall be finalized during detail engineering. |
| 2 | Section Project- Cl No. 2.2.1.1 -II (k ) | Referred clause asked for VMS augmentation with 2 nos of camera for present scope area (Indoor/outdoor). - But There are no line items for VMS augmentation in BPS. Please review & add line items for the same. - Also please arrange to provide the existing VMS layout for GIS hall as well as for 220KV yard. | - Please refer Sl No 1 of Amendment 2. - Make & Model of the existing VMS is Qognify Drawing shall be provided to successful bidder during detailed engineering. Further, as per Clause no 2.4 of the section project: "The bidders are advised to visit the existing substation sites and acquaint themselves with the topography, infrastructure and also the design philosophy". |
| 3 | Electrical plan Layout - C/ENGG/NEW MELLI GIS/GIS/EXTN/LAY/O1 | From the scope marking on the layout drawing we understand following - 2 nos Single tire Tower with 2 nos B1 Beam are under present scope - 2 nos Double tire Tower with 4 nos B2 Beam are under present scope - Present scope line (Rangit-IV Feeder 1 & 2) will be in Lower tire Please confirm our understanding. | 1 & 2. Requirement is ample clear in bidding document. Bidder to quote as per BPS. 3. Confirmed. Scope is clearly indicated in tender GA drawing also. |
| 4 | Section Project- Annexure-1 | As per annexure-1, Existing GIS Interface module drawing supposed to be enclosed along with tender. But same is not available. Please arrange to provide the same as it is required to design present scope bus bar extension module. | Existing GIS of GE make is already equipped with extension piece module but without Isolating link. As per clause II(i)(iii) of Annexure III of section project, " Extension piece (Interface) module, as required to extend existing bus so as to maintain minimum possible inter connection space between GIS supplied under present scope and the GIS being extended." The available details/drawings shall be provided to successful bidder during detailed engineering stage. However, it is the responsibility of bidder to successfully extend the existing GIS. In addition to available details of existing GIS necessary site measurement, gas work and any conductor/consumable etc required shall be in the scope of bidder. Necessary shutdown for same if required shall be arranged by POWERGRID. |
| 5 | Section Project- Cl No. 2.2.1.1 -II (b ) (ii) | FO cable and accessories are required for connection between two differential relay. Please confirm whether dedicated FO cable to be used for line differential protection. | Bidder may quote meeting the requirement of TS & BPS |

| Project | Clarification-2 for GIS portion of Transmission line package TL-01 for Part – A: construction of 220 kV D/C (Twin Moose) Transmission Line from 120 MW Rangit-IV HEP to New Melli Pooling Station and Part – B: Extension of 2 nos. 220 kV GIS bays at New Melli (POWERGRID) GIS S/S under |  |  |
| --- | --- | --- | --- |
| Sl. No. | Reference Document | Query asked by the bidders | POWERGRID reply |
|  | Clause no / Page no |  |  |
| 6 | General | Please arrange to provide the GIS sectional drawing where Bus height is indicated. Same is required to design present scope bus bar extension module. | Drawing for reference to Bus Height is attached. Please refer clause no 2 of Amendment 2 Further, as per Clause no 2.4 of the section project: "The bidders are advised to visit the existing substation sites and acquaint themselves with the topography, infrastructure and also the design philosophy". |
| 7 | General | - Please arrange to provide the existing Crane capacity & hook height. Same can not be identified during site visit. - Please confirm crane extension are not required for present scope. | - Extension of GIS Building as well as Provision of EOT Crane are not envisaged under present scope. Existing Crane Capacity is 5 T & the same is envisaged for use for the movement of modules under present scope. As per Clause no 2.4 of the section project: "The bidders are advised to visit the existing substation sites and acquaint themselves with the topography, infrastructure and also the design philosophy". - Confirmed, crane extension is not envisaged under present scope of work |
| 8 | General | - We presume that only outdoor trench to be extended for present scope from nearest existing cable trench. - Existing trench have sufficient space for cable under present scope. Please confirm. - Please arrange to provide existing cable trench layout drawing (Indoor & Out door) | 1 & 2- Bidder to quote meeting the requirement of TS & BPS 3- Drawing as required, shall be provided to successful bidder during detailed engineering. Further, as per Clause no 2.4 of the section project: "The bidders are advised to visit the existing substation sites and acquaint themselves with the topography, infrastructure and also the design philosophy". |
| 9 | General | We understand that existing AHU is sufficient for present scope area ventilation in GIS hall. Please confirm. | Confirmed |
| 10 | General | Please confirm whether there are any underground facility (like Hydrant pipe/Earth pit/old unloading foundation etc.) are present in the present scope working area. During site visit same is not identified. Also in BPS there are no line items. | Bidder to quote meeting the requirement of TS & BPS |
| 11 | General | Please arrange to provide the existing earth mat layout or mention the earth grid spacing to quantify rise as lot items. | Please refer clause no 2 of Amendment 2 |
| 12 | Volume-II, Technical specifications Part-B, Clause 2.2.1.3 B-1.1 & Price schedule, Sch-3, B | As per referred clause in section project, our scope of work includes modification works such as making necessary arrangement for GIB wall opening, making good flooring after foundation, internal cable trench etc. Whereas there is no separate line item in price schedule for above works, please add separate line item for same. | Only dismantling of concrete shall be payable separately. All other associated works is deemed to be included in respective items for which no extra payment is applicable |

| Project | Clarification-2 for GIS portion of Transmission line package TL-01 for Part – A: construction of 220 kV D/C (Twin Moose) Transmission Line from 120 MW Rangit-IV HEP to New Melli Pooling Station and Part – B: Extension of 2 nos. 220 kV GIS bays at New Melli (POWERGRID) GIS S/S under |  |  |
| --- | --- | --- | --- |
| Sl. No. | Reference Document | Query asked by the bidders | POWERGRID reply |
|  | Clause no / Page no |  |  |
| 13 | Volume-II, Technical specifications Part-B, Clause 2.2.1.3 B | Kindly provide the plan, elevation, section along with the structural detail drawings of the existing GIS Hall building. | Please refer clause no 2 of Amendment 2 |
| 14 | Volume-II, Technical specifications Part-B, Clause 2.2.1.3 B | We request you to provide the existing internal cable trench details (plan & section) inside the 220kV GIS Hall. | Please refer clause no 2 of Amendment 2 |
| 15 | Price schedule, Sch-3, B, 60 | Kindly provide the drawing of Random rubble masonry wall for working out the quantities for tender purpose. | The drawing of RRM wall is in contractor's scope as per clause no 2.2.1.3.B.2.5 & 2.2.1.3.H |
| 16 | Price schedule, Sch-1, B, 54 | Kindly provide the standard drawing of pipe support structure for Wave trap as the same is not available in tender document. | Please refer clause no 2 of Amendment 2 |
| 17 | Section Project- Annexure-1 | Sectional & Interface Drawings of existing GIS. Please provide the same. | Drawings as required ( in PDF format), shall be provided to successful bidder during detailed engineering. Further, as per Clause no 2.4 of the section project: "The bidders are advised to visit the existing substation sites and acquaint themselves with the topography, infrastructure and also the design philosophy". |