| Sl. No. | # Volume/ Section | # Clause No. | # Description | # Bidder’s Query | # POWERGRID Reply |
| --- | --- | --- | --- | --- | --- |
| Volume-II: Technical Specifications |  |  |  |  |  |
| Bay Extension at 400/220kV Maharani Bag GIS Sub-Station |  |  |  |  |  |
|  | VOLUME-II Technical Specification, Section – Project {Rev.00} | 2.1 -> 4 CONTROL & PROTECTION SYSTEM | The existing 400kV and 220kV bus bar protection scheme at Maharani Bag S/s is distributed type REB500 of M/s Hitachi make (Formerly ABB) and it shall be augmented for bays under present scope. Supply and installation of Peripheral units for augmentation of Bus Bar Protection relays is covered under the present scope. | Request to kindly furnish the existing ordering code details of Maharani Bagh s/s Hitachi Busbar PU’s. Existing busbar version (7.50) is very old. | Bidder to quote as per the provisions in bidding document. |
|  | 1.0) Section-Project_SS151 Volume-II Part 5 of 11 | Cl. No. 2.1, A. 2. 19.0 EHV XLPE cable Rev01 | 220kV EHV XLPE Cable The cable shall be 220kV, 1CX2500sq.mm Copper conductor, XLPE insulated as per details in Section: EHV XLPE Cable Rev01. The EHV grade cable shall be single core, …...followed by radial sealing (Metal sheath of Lead alloy ‘E’ / Corrugated Aluminium, (unless otherwise specified in Section Project), ... | Bidder to consider 127/220kV cable (earth grade) for the 220kV EHV cable. Please confirm our understanding. | Bidder understanding is correct. |
| Extension of 400kV Jhatikara Sub-Station |  |  |  |  |  |
|  | VOLUME-II Technical Specification, Section – Project {Rev.00} | 2.2 -> 2 CONTROL & PROTECTION SYSTEM | The existing bus bar protection scheme at Jhatikara S/s is distributed type Micom 741/743 of M/s GE make, and it shall be augmented for bays under present scope. Supply and installation of Peripheral unit is covered under the present scope. All necessary items & components as required, for completion of augmentation of 400kV bus bar protection scheme for bay under present scope shall be provided and bidder to consider the cost of these items & components under respective BPS items | As per CRP Specification Rev-09 "If the bus section is provided then each side of bus section shall have separate set of bus bar protection schemes ". Under present scope 2 nos of bus section added and As per BOQ only Augmentation of existing 400kV bus bar protection scheme only mentioned. Hence, we have not considered new busbar protection for each section, only augmentation of present scope of bays to existing busbar with required PU's applicable. Kindly confirm. | Confirmed |
|  | Price schedule | Mandatory spares |  | As per Annexure-II_Breakup Mandatory Spare document spares applicable for CRP/SAS, however mandatory spares for CRP/SAS not mentioned in price schedule for Jhatikara s/s. Request to kindly amend the BOQ if required. | Bidder to quote as per BPS |
| Bay Extension at 400/220kV Lucknow Sub-Station |  |  |  |  |  |
|  | VOLUME-II Technical Specification, Section – Project {Rev.00} | 2.3 -> 6 CONTROL & PROTECTION SYSTEM | In the present scope, the Bay level IEDs/equipment/Hard wiring to existing RTU panels shall be retained, and station level equipment/network shall be replaced. Existing RTUs hardware (ABB make – RTU 232 & RTU 560) shall be replaced with new BCUs. However, hard wiring of BI/BO and analogue signal to RTU hardware is to be shifted to these new BCUs, keeping the downstream system up to control and relay panels remaining same. After replacement of RTU hardware, the new BCUs, the IEDs (C264) in Extension Rack, IEDs (C264) in NTAMC Rack and IED installed in different panels will report directly to the new SAS. Creation of necessary network as per standard SAS architecture included with TS inter alia including all required Ethernet Switches, LIU, OFC etc. is also included under the present scope. The offered system shall have the capacity to integrate all IEDs/devices mentioned above. The detailed scope of work for SAS Upgradation is as below: | 1) Request to kindly furnish the existing RTU drawings for assessing the RTU replacement work. 2) Kindly confirm panel wise shutdown shall be granted/provided for carrying out RTU replacement work. | 1) Refer our reply to the similar quey in Clarification-II. 2) If required, panel wise shutdown shall be granted/provided for carrying out RTU replacement work. |
|  | VOLUME-II Technical Specification, Section – Project {Rev.00} | 2.3 -> 6.V CONTROL & PROTECTION SYSTEM | Integration of data points (Binary Inputs 1500 Nos., Binary Outputs 500 Nos., Analogue Inputs 250 Nos), of existing RTU's & Aux BCU in upgraded SAS Gateways over IEC-61850 protocol. | We request PGCIL to provide the existing RTU drawings. | Refer our reply to the similar quey in Clarification-II. |
|  | VOLUME-II Technical Specification, Section – Project {Rev.00} | 2.3 -> 6.VI CONTROL & PROTECTION SYSTEM | Necessary up-gradation of firmware of IED’s if required shall be deemed to be included elsewhere. Software for the configuration tool of IEDs shall be handed over by the vendor after execution of the contract. | As per details collected from site some IED's are not 61850 compatibles. We request PGCIL to change applicable relays to IEC 61850 to integrate to proposed SAS. We understand integration of IED's to proposed SAS applicable only for 61850 relays. Remaining relays will not be considered for SAS integration. Kindly confirm. | Bidder to quote as per the provisions in bidding document. |
|  | Price schedule | CRP for conventional 420kV bays | 400KV CIRCUIT BREAKER RELAY PANEL | As per section project and SLD one incomplete diameter with main and tie bay is added under present scope. However, in price schedule CB relay panel qty for 400kV is mentioned as 1 instead of 2 Nos. Request to kindly update the Price schedule. | Refer our reply to the similar quey in Clarification-II. |