| Sl. No. |  | # Volume/ Section/ Description | # Clauses | # Bidder’s Query | # POWERGRID Reply |
| --- | --- | --- | --- | --- | --- |
| Volume-I: Conditions of Contract |  |  |  |  |  |
|  | ITB 24.1 (c), BDS, Section-III, |  | The Time for Completion shall be as under: Description; Duration in Months from the date of Notification of Award. Taking Over by the Employer upon successful Completion of. 400kV GIS Substation Package SS-151 (including Transformer) for:. (i) Extension of 400/220kV Maharani Bagh (PG) GIS S/s and 400/220/33kV, 500 MVA 3-Ph ICT at Maharani Bagh (PG) {with oil to SF6 bushing) under Augmentation of transformation capacity at 400/220kV Maharani Bagh (PG) S/s (GIS) in Delhi by 1x500 MVA, 400/220kV ICT (5th); 20 (Twenty) Months. (ii) 400kV Sectionalization bay (GIS) at 765/400kV Jhatikara (PG) S/s under Implementation of 400kV Sectionalization bay (GIS) at 765/400kV Jhatikara (PG) S/s to interconnect both 400kV sections in the event of contingency; 14 (Fourteen) Months. (iii) Extension of 400/220kV Lucknow (PG) S/s under Augmentation of transformation capacity at 400/220kV Lucknow (PG) S/s by 1x500 MVA, 400/220kV ICT (3rd) along with associated bays.; 20 (Twenty) Months. | Considering the current market availability and delivery timeline for a 1x500 MVA, 400/220kV ICT, the proposed completion period of 20 months for Maharanibagh substation is not feasible. We therefore request M/s PGCIL to kindly consider extending the project completion timeline to a minimum of 36 months. OR Alternatively, since PGCIL is free issuing the 500MVA ICT for Lucknow substation. Hence, we request PGCIL to exclude the supply and erection of the 1x500 MVA, 400/220kV ICT from the present scope of work. We kindly request M/s. PGCIL to review and accept our request. | Provisions of the Bidding Documents remains unchanged |
| Volume-II: Technical Specifications |  |  |  |  |  |
| ICT-5 Maharani Bagh |  |  |  |  |  |
|  |  | A.1, 2.1, Section-Project_SS151 | Any modification required in the existing 400kV and 220kV GIS building for extension of GIS Buses and taking outside the building is also deemed to be included. | (i) We understand that Same 400kV & 220KV GIS buses is to be extended for Present Outdoor GIS bays. Separate bus is not envisaged. (ii) Please confirm the IP requirement for Outdoor GIS & LCC. | (i) Bidder understanding is correct. (ii)For IP requirement for Outdoor GIS & LCC refer relevnt clause of TS. |
|  |  | A.1 (K), 2.1, Section-Project_SS151 | Outdoor Local Control Cabinet (LCC), GIS Equipment Marshaling boxes/operating mechanism boxes & terminal boxes shall be made of stainless steel of at least 1.5 mm thick or aluminum enclosure of at least 1.6 mm thick and shall be dust, water and vermin proof. Stainless steel used shall be of grade SS304 (SS316 for coastal area) | Kindly confirm the Canopy requirement for LCC, if any. | Bidder to quote as per the provisions in bidding document. |
|  |  | 4, CONTROL & PROTECTION SYSTEM, 2.1, Section-Project_SS151 | existing 400kV and 220kV bus bar protection scheme at Maharani Bag S/s is distributed type REB500 of M/s Hitachi make (Formerly ABB) and it shall be augmented for bays under present scope. | (i) Please share existing SAS Architecture. (ii) We understand that existing CU has the spares available to cater present bays requirement and PU to be supplied for present scope. (iii) Please confirm if any additional License is required. | i) SAS Architecture Shall be provided during detail engineering. ii) & iii) Bidder to quote as per the provisions in bidding document. . |
|  |  | 4, CONTROL & PROTECTION SYSTEM, 2.1, Section-Project_SS151 | CRP panel for bays under present scope shall be placed inside the New Switchyard Panel Room. | Please share the distance b/w - (i) Existing ACDB & DCDB to New Switchyard Panel Room (ii) Existing SAS Panel to New Switchyard Panel Room | Bidder to quote as per bidding provisions. For better understanding bidder may visit the site. |
|  |  | Clause-3, 2.1, Section-Project_SS151 | Existing three numbers of 3-phase ICT are with conventional type of RTCC panel, which are to be dismantled and same is to be handed over to POWERGRID | (i) We understand that in One number RTCC panel, all Six (6) numbers RTCC relays to be installed. Kindly confirm our understanding. (ii) Kindly confirm location to keep dismentled RTCC Panels. (iii) Kindly confirm who shall be responsible for RTCC integration with SAS and re-wiring. (iv) We understand that if any supervision for Power Transformer & RTCC from Existing OEMs is required then same shall be provided by PGCIL. | i) AS per prevailing practice 4 Nos RTCC relays are mounted in one panel, Bidder is requested to follow the same. ii)This Shall be informed during detail engineering in consultation with POWERGRID site office. iii) Bidder shall be responsible for RTCC integration with SAS and re-wiring. iv) Bidder shall be responsible for supervision for Power Transformer & RTCC from Existing OEMs. |
|  |  | Clause-3, 2.1, Section-Project_SS151 | The LV side (33kV) of 400/220/33kV Transformer shall have conventional AIS type termination | Please confirm where to connect 33kV side of Power Transformer. | Bidder to quote as per the provisions in bidding document. |
|  |  | Clause-10, 2.1, Section-Project_SS151 | Fire protection system including HVWS & Hydrant system …..............The piping for fire protection system shall be extended from nearest available header tapping point. | Please provide the existing Hydrant System details & Pipe Layout. | Existing Hydrant System details & Pipe Layout. shall be provided during detail engineering. |
|  |  | General | - | Kindly confirm the avaibility of ports of existing gateway for intergration of 400KV & 220kV bays under present scope. Kindly provide existing gatewaydetails. | Bidder to quote as per bidding provisions. For better understanding bidder may visit the site. |
| Bus Sec Bay Jhatikara |  |  |  |  |  |
|  |  | A.1, 2.2, Section-Project_SS151 | The existing 400kV Jhatikara Substation is of AIS type. The proposed extension for 400 kV Bays is to be done through outdoor GIS. The 400kV GIS bays under present scope shall be placed outdoor at suitable location in 400kV Switchyard. | (i) We understand that Same 400kV GIS buses is to be extended for Present Outdoor AIS bays. Separate bus is not envisaged. (ii) Please confirm the | (i) 400kV Jhatikara substation is of AIS type. There is no existing GIS. Bidder to quote as per bidding provisions. (ii)For IP requirement for Outdoor GIS & LCC refer relevnt clause of TS. |
|  |  | A.1 (j), 2.2, Section-Project_SS151Section-Project_SS151 | Outdoor Local Control Cabinet (LCC), GIS Equipment Marshaling boxes/operating mechanism boxes & terminal boxes shall be made of stainless steel of at least 1.5 mm thick or aluminum enclosure of at least 1.6 mm thick and shall be dust, water and vermin proof. Stainless steel used shall be of grade SS304 (SS316 for coastal area) | Kindly confirm the Canopy requirement for LCC, if any. | For Canopy requirement for LCC refer relevnt clause of TS. |
|  |  | Clause -2, 2.2, Section-Project_SS151 | The existing bus bar protection scheme at Jhatikara S/s is distributed type Micom 741/743 of M/s GE make, and it shall be augmented for bays under present scope. Supply and installation of Peripheral unit is covered under the present scope | (i) Please share existing SAS Architecture. (ii) We understand that existing CU has the spares available to cater present bays requirement and PU to be supplied for present scope. (iii) Please confirm if any additional License is required. | i) SAS Architecture Shall be provided during detail engineering. ii) &iii) Bidder to quote as per the provisions in bidding document. . |
|  |  | Clause-4, 2.2, Section-Project_SS151 | CRP panel for bays under present scope shall be placed inside the New Switchyard Panel Room. | Please share the distance b/w - (i) Existing ACDB & DCDB to New Switchyard Panel Room (ii) Existing SAS Panel to New Switchyard Panel Room | Bidder to quote as per bidding provisions. For better understanding bidder may visit the site. |
|  |  | Substation Automation system | General | Kindly confirm the avaibility of ports of existing gateway for intergration of 400KV & 220kV bays under present scope. Kindly provide existing gatewaydetails. | Bidder to quote as per bidding provisions. Details shall be provided during detail engineering. |
| ICT Bay 400/220kV Lucknow SS |  |  |  |  |  |
|  |  | A.1, 2.3, Section-Project_SS151 | The existing 400/220kV Lucknow Substation is of AIS type. The proposed extension for 400 kV Bays is to be done through outdoor GIS and the Extension of 220 kV Bays is to be done through AIS. | (i) We understand that Same 400kV GIS buses is to be extended for Present Outdoor AIS bays. Separate bus is not envisaged. (ii) Please confirm the IP requirement for Outdoor GIS & LCC. | (i) 400kV Lucknow substation is of AIS type. There is no existing GIS. Bidder to quote as per bidding provisions. (ii)For IP requirement for Outdoor GIS & LCC refer relevnt clause of TS. |
|  |  | A.1 (i), 2.3, Section-Project_SS151 | Outdoor Local Control Cabinet (LCC), GIS Equipment Marshaling boxes/operating mechanism boxes & terminal boxes shall be made of stainless steel of at least 1.5 mm thick or aluminum enclosure of at least 1.6 mm thick and shall be dust, water and vermin proof. Stainless steel used shall be of grade SS304 (SS316 for coastal area) | Kindly confirm the Canopy requirement for LCC, if any. | For Canopy requirement for LCC refer relevnt clause of TS. |
|  |  | 4 (d), 2.3, Section-Project_SS151 | DIGITAL RTCC Panel: RTCC Panel is to be supply with 4 nos. digital RTCC relay (one each for Two numbers 3-Ph existing ICT, one for ICT under present scope and one Spare). | (i) Since Power Transformer are being free issued by the PGCIL. Hence we requesting to supply the RTCC also. Which includes co-ordination from Transformer OEM and RTCC suppliers for SCADA integration. Please accept. (ii) We confirm the dismentaling of existing RTCC shall be done by the bidder. Please provide the location to keep dismentled RTCC. | Bidder to quote as per bidding provisions. |
|  |  | Clause-5, 2.3, Section-Project_SS151 | The existing 400kV and 220 kV bus bar protection scheme at Lucknow S/s is distributed type P741/743 of M/s GE make, and it shall be augmented for bays under present scope. Supply and installation of Peripheral unit is covered under the present scope | (i) Please share existing SAS Architecture. (ii) We understand that existing CU has the spares available to cater present bays requirement and PU to be supplied for present scope. (iii) Please confirm if any additional License is required. | i) SAS Architecture Shall be provided during detail engineering. ii) &iii) Bidder to quote as per the provisions in bidding document. . |
|  |  | Clause-5, 2.3, Section-Project_SS151 | CRP panel for bays under present scope shall be placed inside the New Switchyard Panel Room. | Please share the distance b/w - (i) Existing ACDB & DCDB to New Switchyard Panel Room (ii) Existing SAS Panel to New Switchyard Panel Room | Bidder to quote as per bidding provisions. For better understanding bidder may visit the site. |
|  |  | Clause-6, 2.3, Section-Project_SS151 | Integration of data points | BI, BO, AI inputs given in section project shall be integrated in New SAS. Bidder needs not to consider any additional data tags. Kindly confirm. | Bidder to quote as per bidding provisions. |