| Sl. No. |  | # Volume/ Section |  | # Clause No. | # Description | # Bidder’s Query | # POWERGRID Reply |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Volume-II (Technical Specifications) |  |  |  |  |  |  |  |
|  |  | Technical Specification GTR |  |  | Construction power | Being an existing site, power is available hence We understand PGCIL shall be providing construction power on chargeable basis at one point near to substation building. | Bidder may refer Technical Specification GTR: clause 14.3 for better understanding |
|  | I Bay Extension at 400/220kV Maharani Bag GIS Sub-Station |  |  |  |  |  |  |
|  |  | 1.0) Section-Project_SS151 Price_schedule |  | Cl No. 2.1, A. 2 220kV EHV XLPE Cable Line item sl.no. 22 & 23 | 220kV, EHV XLPE cable (Single run each for R, Y, B phase) and Cable Termination kit along with all accessories shall be supplied as per BPS. The 220kV, EHV XLPE cable shall be laid in buried cable trench from 220kV side of ICT#5 up to 220kV GIS bay is under present scope. The cable shall be 220kV, 1CX2500sq.mm Copper conductor, XLPE insulated as per details in Section: EHV XLPE Cable Rev01. SET : 3 | We understand that 1 set comprises of 1 no. cable per phase. However, bidder to consider 2 nos. cable per phase for the 500MVA transformer involved. Please confirm our understanding for estimation of structure and other accessories. | Single Run per phase of 220kV cable is envisaged, as it is 2500sqmm CU cable. Bidder to quote as per the provisions in bidding document. |
|  |  | 1.0) Section-Project_SS151 |  | Cl No. 2.1, A. 3 Cl. No. DIGITAL RTCC | Necessary re-wiring, cabling is also under present scope of work. | We understand that the existing cable for 4 nos. RTCC can be re-used. Please confirm our understanding. | If existing cables are in reusable condition, it may be used after joint verification with POWERGRID Site In-charge. |
|  |  | 1.0) Section-Project_SS151 Site visit |  | Cl No. 2.1, A. 13 LT SWITCHGEAR i) Existing ACDB-I & II | Existing ACDB-I & II shall be augmented under present scope by providing ….. | During site visit we have not found any vacant feeder module on ACDB-I and ACDB-II for installation of 300A MCCB outgoing feeder. We also have not found any space for installation of extension ACDB. Please provide the actual location of installation of outgoing 300A MCCB and extension board for assessing cable requirement. | Actual location of installation of outgoing 300A MCCB shall be provided during detailed engineering, For the purpose of estimation of cable kindly consider extension from existing ACDB/DCDB Room Bidder to quote as per the provisions in bidding document. |
|  |  | 1.0) Section-Project_SS151 Site visit |  | Cl No. 2.1, A. 13 LT SWITCHGEAR ii) Existing DCDB-I & II | Existing DCDB-I & II shall be augmented under present scope by providing ….. | During site visit we have not found any vacant feeder module on DCDB-I and DCDB-II for installation of 100A MCCB outgoing feeder. We also have not found any space for installation of extension DCDB. Please provide the actual location of installation of outgoing 100A MCCB and extension board for assessing cable requirement. | Actual location of installation of outgoing 100A MCCB shall be provided during detailed engineering, For the purpose of estimation of cable kindly consider extension from existing ACDB/DCDB Room Bidder to quote as per the provisions in bidding document. |
|  |  | Price Schedule: Sch-1 |  | I Sl. No. 8 | 420KV,4000A, 63KA, 3-PHASE GIS EXTENSION PIECE (INTERFACE) MODULESUITABLE FOR EXTENDING EXISTING HYOSUNG MAKE GIS BUS BAR/DUCT AS PERTECHNICAL SPECIFICATION | The fault level of existing 400kV GIS is 50kA for 1 sec. hence we understand that the short circuit rating of GIS under present scope also to be considered 50kA for 1 sec. Please confirm our understanding. | Bidder to quote as per the provisions in bidding document. |
|  |  | 1.0) Section-Project_SS151 19.0 EHV XLPE cable Rev01 |  | Cl. No. 2.1, A. 2. Cl. No. 34 | The Item “220KV HV POWER CABLE” of BPS includes all the bonding cable, link boxes, Sheath Voltage Limiters (SVLs) etc. (jointing kit is not envisaged). DISTRIBUTED TEMPERATURE MONITORING SYSTEM (DTS) | Clause 34 of EHV cable specification asks for DTMS System but the same is not mentioned in section project and BPS. We understand that the DTS system is not to be considered by bidder. Please confirm our understanding. | Bidder's understanding is correct. |
|  |  | General |  |  | Below ground earthmat layout | Please provide existing earthmat layout. | Existing Earthmat Layout shall be provided during detail engineering. |
|  |  | Price Schedule: Sch-1 |  | I Sl. No. 14 | 245KV,3000A, 50KA, 3-PHASE GIS EXTENSION PIECE (INTERFACE) MODULESUITABLE FOR EXTENDING EXISTING HYOSUNG MAKE GIS BUS BAR/DUCT AS PERTECHNICAL SPECIFICATION | The fault level of existing 220kV GIS is 40kA for 1 sec. hence we understand that the short circuit rating of GIS under present scope also to be considered 40kA for 1 sec. Please confirm our understanding. | Bidder to quote as per the provisions in bidding document. |
|  |  | Price Schedule: Sch-1 |  | I Sl. No. 19 | Scissor Lift | The scope of work is for outdoor GIS, hence, we understand that Scissor lift not to be considered. Please confirm our understanding. | Bidder to quote as per the provisions in bidding document. |
|  |  | Price Schedule: Sch-1 & 1.0) Section-Project_SS151' |  | I Sl. No. 31 & Cl. No. 2.1, A. 15 | VMS scope | Please confirm the make and model of existing VMS system. | Make and Model of existing VMS system shall be provided during detail engineering. |
|  |  | Site visit |  |  | 400kV GIS hall | During site visit we have found 2.55mtrs. Space is available between Y-Ph main bus to the wall / rolling shutter of the 400kV GIS hall. This space will be reduced after installation of GIS extension piece (interface) modules for GIS busbar extension module. Please confirm our understanding. | Bidder to quote as per the provisions in bidding document. |
|  |  | 1.0) Section-Project_SS151 Volume-II Part 5 of 11 |  | Cl. No. 2.1, A. 2. 19.0 EHV XLPE cable Rev01 | 220kV EHV XLPE Cable The cable shall be 220kV, 1CX2500sq.mm Copper conductor, XLPE insulated as per details in Section: EHV XLPE Cable Rev01. The EHV grade cable shall be single core, …...followed by radial sealing (Metal sheath of Lead alloy ‘E’ / Corrugated Aluminium, (unless otherwise specified in Section Project), ... | Please confirm the metal sheath whether it will be Lead alloy 'E' or corrugated Aluminium as the same is not specified in Section Project. | Refer Amendment No-05 |
|  |  | Volume-II_Part_1_of_11/ 1.0) Section-Project_SS151 & Bid Price Schedule |  | 2.3 Name of Substation: Bay Extension at 400/220kV Maharani Bag GIS Sub-Station 3. (b) | DIGITAL RTCC Panel: RTCC Panel is to be supply with 6 nos. digital RTCC relay (one each for four numbers 3-Ph existing ICT, one for ICT under present scope and one Spare). Existing three numbers of 3-phase ICT are with conventional type of RTCC panel, which are to be dismantled and same is to be handed over to POWERGRID. Installation of above mentioned Digital RTCC panel, also include scope of dismantling existing RTCC panels. Necessary re-wiring, cabling is also under present scope of work | 1) We understand that four units of 3-phase ICTs, instead of three, are associated with the conventional type RTCC panel. These panels are to be dismantled and handed over to POWERGRID. Kindly confirm. 2) Kindly confirm the location for keeping this dismantled panel. 3) We understand that no wiring modification in existing OLTC DM / Transformer MB is in bidders scope. Kindly confirm. | 1) Bidder to quote as per the provisions in bidding document. For better understanding bidder to refer clause 2.1.A).3 2) This Shall be informed during detail engineering in consultation with POWERGRID site office. 3) Bidder to quote as per the provisions in bidding document. |
|  |  | BPS/Sch-1 & Section Project |  | S. No.37 & Cl No. 10 Page 9 of 30 | Fire Detection and Alarm System for Switchyard Panel Room of 6 m length Smoke detection, Fire alarm & Annunciation System and Fire Extinguishers for Switchyard Panel Room. | We understand that spare capacities in the existing Main Fire Alarm Panel/Annunciation Panel shall be used for the present scope of extension work and accordingly new Fire Alarm Panel/Annunciation panel is not envisaged as same is not categorically specified either in Section project or in Price schedule. Kindly confirm our understanding. | New Fire Annunciation panel is not envisaged, however Augmentation of existing Fire Annunciation panel if required for present scope shall be in the scope of contractor. |
|  |  | 1.0) Section-Project_SS151 |  | Clause no: 2.17.c.ix Page no 11/30 | Dismantling and re-erection of solar panels | During site visit we have not found any solar panels installed on existing store roof top. Hence, we understand that dismantling and re-erection of solar panels are not in scope. Please confirm our understanding. | Bidder to quote as per the provisions in bidding document. |
|  |  | 1.0) Section-Project_SS151 |  | Clause no: 2.17.c.ix Page no 11/30 | Dismantling and re-erection of solar panels | If above scope is applicable, then we understand that all Solar panels and associated structures shall be provided in complete and in healthy /functional condition by PGCIL. With this bidder scope "if applicable" shall be limited to re erection only. Please confirm. | Bidder to quote as per the provisions in bidding document. |
|  |  | 1.0) Section-Project_SS151 |  | Clause no: 2.17.c.x Page no 11/30 | Dismantling of existing spare ICT platform | We understand that existing Transformer plinth shall be used for outdoor GIS Plinth. Please confirm our understanding. | Bidders understanding is not correct. Bidder to quote as per the provisions in bidding document. |
|  |  | 1.0) Section-Project_SS151 |  | Clause no: 2.0 Page no 10/91 | 2.0 GEOTECHNICAL INVESTIGATION: | We understand that PGCIL will provide Soil Investigation report during execution stage. Kindly confirm. | To be provided to the successful bidder during detail engineering. |
|  |  | 16.0 Civil Works Rev 12 |  | Clause no: 20.3 Page no 68/91 | DISPOSAL OF MATERIALS: | Kindly confirm disposal area for discarded material and distance with respect to Maharani bagh substation. | Disposal area shall be provided to the successful bidder. |
|  |  | 16.0 Civil Works Rev 12 |  | Clause no: 24.22 Page no 87/91 | DRAINS The mode of measurement for drain shall be running meter. | We understand that, for project requirement existing drains may need to be dismantled. We also understand that reconstruction of dismantled drain will be paid through respective line items at Sch-3; Sl. No. A. 69, 70, 71 of Maharani bagh substation. Please confirm. | Drains damaged as a result of construction activities carried out in accordance with the approved drawings shall be reconstructed and will be eligible for payment. However, any damage arising from equipment movement or other incidental activities not specified in the drawings shall also be reinstated by the contractor, but no additional payment shall be made for such works. |
|  |  | 16.0 Civil Works Rev 12 |  | Clause no: 20.4 Page no 69/91 | SITE CLEARANCE The work shall consist of numbering of trees, removing and disposing of all materials such as trees, bushes, woods, shrubs, grass, stumps, rubbish, rank vegetation, roots, foreign materials, etc., which in the opinion of the Engineer-in-Charge are.... Clearing and grubbing item is not payable and the same shall be deemed to be included in the earth work in excavation and filling. Trees having girth above 30 cm are not in the scope of Contractor. | During site visit, we observed that, Peepal trees are present at extension area at Maharani bagh. Kindly confirm that, necessary permission required for cutting the Trees will be facilitated by PGCIL to successful Bidder. | Bidder to quote as per the provisions in bidding document. |
|  |  | General |  |  | Way access | Clear way access shall be made available by PGCIL with adequate shutdown to the extension portion. Please confirm. | Bidder to quote as per the provisions in bidding document. |
|  |  | General |  |  | Shut down | Necessary shutdown shall be provided by PGCIL for safe working meeting EHS guidelines as and when required. Please confirm. | Noted. |
|  |  |  | II Extension of 400kV Jatikara Sub-Station |  |  |  |  |
|  |  | Price Schedule: Sch-1 |  | II Sl. No. 13 | VMS scope | Please confirm the make and model of existing VMS system. | Make and Model of existing VMS system shall be provided during detail engineering. |
|  |  | Price Schedule: Sch-1 |  | II Sl. No. 20 | Illumination System for switchyard panel room of 6 m length. | We understand that individual SPR of 6x4.5M shall be considered for each side of GIS bus section bay. Please confirm our understanding. | Bidders understanding is not correct. Bidder to quote as per the provisions in bidding document. |
|  |  | BPS/Sch-1 & Section Project |  | S. No.17 & Cl No. 8 Page 15 of 30 | Fire Detection and Alarm System for Switchyard Panel Room of 6 m length Fire Protection System Smoke detection, Fire alarm & Annunciation System and Fire Extinguishers for Switchyard Panel Room. | We understand that spare capacities in the existing Main Fire Alarm Panel/Annunciation Panel shall be used for the present scope of extension work and any new Fire Alarm Panel/Annunciation panel is not in bidder's scope of work. Kindly confirm. | New Fire Annunciation panel is not envisaged, however Augmentation of existing Fire Annunciation panel if required for present scope shall be in the scope of contractor. |
|  |  | 1.0) Section-Project_SS151 |  | Clause no: 2.2A.1 Page no 25/30 | The existing 400kV Jatikara Substation is of AIS type. The proposed extension for 400 kV Bays is to be done through outdoor GIS. The 400kV GIS bays under present scope shall be placed outdoor at suitable location in 400kV Switchyard. 400kV Main Buses under present scope, are to be extended from the existing 400kV AIS buses. | Request PGCIL to provide the following inputs and confirm: Kindly provide sectional drawing of 400kV AIS substation where SF6 to Air Bushing connection envisaged. | Same has been tentatively marked in GA drawing. For better understanding bidder may visit the site. |
|  |  | 1.0) Section-Project_SS151 |  | Clause no: 2.2A.1 Page no 25/30 | The existing 400kV Jatikara Substation is of AIS type. The proposed extension for 400 kV Bays is to be done through outdoor GIS. The 400kV GIS bays under present scope shall be placed outdoor at suitable location in 400kV Switchyard. 400kV Main Buses under present scope, are to be extended from the existing 400kV AIS buses. | We understand that Soil Investigation report will be provided by PGCIL during execution stage and conducting soil investigation is not in bidder scope. Please confirm. | Soil Investigation report shall be provided during detail engineering. |
|  |  | General |  |  | Below ground earthmat layout | Please provide existing earthmat layout. | Existing Earthmat Layout shall be provided during detail engineering. |
|  |  | 16.0 Civil Works Rev 12 |  | Clause no: 24.22 Page no 87/91 | DRAINS The mode of measurement for drain shall be running meter. | We understand that, for project requirement existing drains may need to be dismantled. We also understand that reconstruction of dismantled drain will be paid through respective line items at Sch-3; Sl. No. B. 29, 30,31 & 32 of Jatikara substation. Please confirm. | Drains damaged as a result of construction activities carried out in accordance with the approved drawings shall be reconstructed and will be eligible for payment. However, any damage arising from equipment movement or other incidental activities not specified in the drawings shall also be reinstated by the contractor, but no additional payment shall be made for such works. |
|  |  | General |  |  | Way access | Clear way access shall be made available by PGCIL with adequate shutdown to the extension portion. Please confirm. | Bidder to quote as per the provisions in bidding document. |
|  |  | General |  |  | Shut down | Necessary shutdown shall be provided by PGCIL for safe working meeting EHS guidelines as and when required. Please confirm. | Noted. |
|  |  |  | III Bay Extension at 400/220kV Lucknow Sub-Station |  |  |  |  |
|  |  | 1.0) Section-Project_SS151 Site visit |  | Cl No. 2.3, A. 14 LT SWITCHGEAR i) Existing ACDB-I & II | Existing ACDB-I & II shall be augmented under present scope by providing ….. | During site visit we have not found any vacant feeder module on ACDB-I and ACDB-II for installation of 300A MCCB outgoing feeder. We also have not found any space for installation of extension ACDB. Please provide the actual location of installation of outgoing 300A MCCB and extension board for assessing cable requirement. | Actual location of installation of outgoing 300A MCCB shall be provided during detailed engineering, For the purpose of estimation of cable kindly consider extension from exisiting ACDB/DCDB Room Bidder to quote as per the provisions in bidding document. |
|  |  | 1.0) Section-Project_SS151 Site visit |  | Cl No. 2.3, A. 14 LT SWITCHGEAR ii) Existing DCDB-I & II | Existing DCDB-I & II shall be augmented under present scope by providing ….. | During site visit we have not found any vacant feeder module on DCDB-I and DCDB-II for installation of 100A MCCB outgoing feeder. We also have not found any space for installation of extension DCDB. Please provide the actual location of installation of outgoing 100A MCCB and extension board for assessing cable requirement. | Actual location of installation of outgoing 100A MCCB shall be provided during detailed engineering, For the purpose of estimation of cable kindly consider extension from exisiting ACDB/DCDB Room Bidder to quote as per the provisions in bidding document. |
|  |  | 1.0) Section-Project_SS151 |  | Cl No. 2.3, A. 15 | VMS scope | Please confirm the make and model of existing VMS system. | Make and Model of existing VMS system shall be provided during detail engineering. |
|  |  | Volume-II_Part_1_of_11/ 1.0) Section-Project_SS151 & Bid Price Schedule |  | 2.3 Name of Substation: Bay Extension at 400/220kV Lucknow Sub-Station 6. SUBSTATION AUTOMATION SYSTEM: (XIV.) | Lucknow substation envisaged for SAS upgradation/replacement under present scope is existing Substation under O&M. Existing SAS architecture, SLD drawing of the substation, List of Existing IEDs are enclosed as Annexure-VI, which shall be further engineered by the bidder. | We have not received the Existing SAS architecture / Annexure-VI along with bidding document as mentioned in Section Project. Request you to kindly furnish the same. | Refer Amendment No-05 |
|  |  | Volume-II_Part_1_of_11/ 1.0) Section-Project_SS151 & Bid Price Schedule |  | 2.3 Name of Substation: Bay Extension at 400/220kV Lucknow Sub-Station 4. (d) | DIGITAL RTCC Panel: RTCC Panel is to be supply with 4 nos. digital RTCC relay (one each for Two numbers 3-Ph existing ICT, one for ICT under present scope and one Spare). Existing three numbers of 3-phase ICT are with conventional type of RTCC panel, which are to be dismantled and same is to be handed over to POWERGRID. Installation of above mentioned Digital RTCC panel, also include scope of dismantling existing RTCC panels. Necessary re-wiring, cabling is also under present scope of work. | 1) We understand that only two units of 3-phase ICTs, instead of three, are associated with the conventional type RTCC panel. These are to be dismantled and handed over to POWERGRID. Kindly confirm. 2) Kindly confirm the location for keeping this dismantled panel. 2) We understand that no wiring modification in existing OLTC DM / Transformer MB is in bidders scope. Kindly confirm. | 1) Bidder to quote as per the provisions in bidding document. For better understanding bidder to refer clause 2.1.A).4 2) This Shall be informed during detail engineering in consultation with POWERGRID site office. 3) Bidder to quote as per the provisions in bidding document. |
|  |  | Volume-II_Part_7_of_11 / Bid Price Schedule |  | Lucknow SLD-GA | 400KV CIRCUIT BREAKER RELAY PANEL - 1 Nos. | We understand that "400KV CIRCUIT BREAKER RELAY PANEL" shall be required for 400kV side of ICT and for 400kV Tie bay. Kindly confirm our understanding. | Refer Amendment No-05 |
|  |  | General |  |  | Below ground earthmat layout | Please provide existing earthmat layout. | Existing Earthmat Layout shall be provided during detail engineering. |
|  |  | Volume-II_Part_7_of_11 / Bid Price Schedule |  | Bid Price Schedule - Schedule 3 Lucknow sl. No 65 | Switchyard Panel Room - Civil Works. All civil works as per drawing and specifications complete, including - brickwork, finishing(external and internal), windows etc. However, excavation, PCC, RCC and reinforcement shall be paid separately as per BPS. - 30 M2 | We understand that present scope 400kV & 220kV CRP will be placed in the same present scope SPR. Kindly confirm. | Confirmed |
|  |  | BPS/Sch-1 & Section Project |  | S. No.40 & Cl No. 11 Page 23 of 30 | Fire Detection and Alarm System for Switchyard Panel Room of 6 m length Fire Protection System Smoke detection, Fire alarm & Annunciation System and Fire Extinguishers for Switchyard Panel Room. | We understand that spare capacities in the existing Main Fire Alarm Panel/Annunciation Panel shall be used for the present scope of extension work and any new Fire Alarm Panel/Annunciation panel is not in bidder's scope of work. Kindly confirm. | New Fire Annunciation panel is not envisaged, however Augmentation of existing Fire Annunciation panel if required for present scope shall be in the scope of contractor. |
|  |  | 1.0) Section-Project_SS151 |  | Clause no: 2.3.17.B.v.i Page no 25/30 | (v) Site levelling work: (i) The item site levelling works includes Contouring of whole plot area within the boundary as per technical specification. The final area of levelling may be less than the whole plot area, which will be decided during detailed engineering. (iii)Mode of measurement of this item is in Cum of earthwork as per BOQ and technical specification. The contouring of the plot area in scope as per technical specification is also deemed to be included in quoted rates of this item. | Since contouring of whole plot area of Lucknow substation is in scope and further cost to be included in " Cum of earthwork" thereby request PCGIL to provide whole plot area with dimensional details or area in 'sqm' for bid stage assessment. | Site levelling and contouring are included in the bidder’s scope for the current works. However, the exact area will be finalized during detailed engineering. |
|  |  | 16.0 Civil Works Rev 12 |  | Clause no: 20.4 Page no 69/91 | SITE CLEARANCE The work shall consist of numbering of trees, removing and disposing of all materials such as trees, bushes, woods, shrubs, grass, stumps, rubbish, rank vegetation, roots, foreign materials, etc., which in the opinion of the Engineer-in-Charge are.... Clearing and grubbing item is not payable and the same shall be deemed to be included in the earth work in excavation and filling. Trees having girth above 30 cm are not in the scope of Contractor. | We understand that, extension are of Lucknow substation is full of bushes and trees. We understand that, Clearing and grubbing item is not payable and the same shall be deemed to be included in the earth work in excavation and filling. Also confirm that, necessary permission required for cutting the Trees will be facilitated by PGCIL to successful Bidder Please confirm. | The bidder may quote as per the provisions of the bidding documents |
|  |  | 1.0) Section-Project_SS151 |  | Clause no: 2.3.A.1 Page no 18/30 | The existing 400/220kV Lucknow Substation is of AIS type. The proposed extension for 400 kV Bays is to be done through outdoor GIS and the Extension of 220 kV Bays is to be done through AIS. | Request PGCIL to provide the following inputs and confirm: 1. Beam of 220kV Main bus Gantry is extendable, kindly confirm. 2. Kindly provide sectional drawing of both 400kV and 220kV AIS substation. | 1) Refer Amendment No-05 2) Sectional drawing of both 400kV and 220kV AIS substation shall be provided during detailed engineering. |
|  |  | 1.0) Section-Project_SS151 |  | Clause no: 2.3.A.1 Page no 18/30 | The existing 400/220kV Lucknow Substation is of AIS type. The proposed extension for 400 kV Bays is to be done through outdoor GIS, and the Extension of 220 kV Bays is to be done through AIS. | We understand that PGCIL will provide Soil Investigation report during execution stage. Kindly confirm. | Soil Investigation report shall be provided during detail engineering. |
|  |  | 16.0 Civil Works Rev 12 |  | Clause no: 24.22 Page no 87/91 | DRAINS The mode of measurement for drain shall be running meter. | We understand that, for project requirement existing drains may need to be dismantled. We also understand that reconstruction of dismantled drain will be paid through respective line items at Sch-3; Sl. No. C. 61, 62, 63 & 64 of Jatikara substation. Please confirm. | Drains damaged as a result of construction activities carried out in accordance with the approved drawings shall be reconstructed and will be eligible for payment. However, any damage arising from equipment movement or other incidental activities not specified in the drawings shall also be reinstated by the contractor, but no additional payment shall be made for such works. |
|  |  | General |  |  | Way access | Clear way access shall be made available by PGCIL with adequate shutdown to the extension portion. Please confirm. | Bidder to quote as per the provisions in bidding document. |
|  |  | General |  |  | Shut down | Necessary shutdown shall be provided by PGCIL for safe working meeting EHS guidelines as and when required. Please confirm. | Noted. |