| Sl. No. | # Volume/ Section | # Clause No. | # Description | # Bidder’s Query | # POWERGRID Reply |
| --- | --- | --- | --- | --- | --- |
| Volume-II (Technical Specifications) |  |  |  |  |  |
| I | Bay Extension at 400/220kV Maharani Bag GIS Sub-Station |  |  |  |  |
|  | 3.0 GIS Rev-5A | Cl. No. 11.3.10 Pg. No. 44/105 | The arrestor enclosure shall be vertically or horizontally mounted to suit the layout of the switchgear as suggested by the supplier and each arrestor shall be fitted with a Online continuous resistive leakage current monitoring system. The system shall be provided with an interface to integrate with the substation automation system. | Please note that we are considering an Online current leakage monitoring transducer with Modbus output for 420kV & 245kV Maharani bagh GIS LA in our offer. Please let us know if any additional Online monitoring systems are required for the present scope. | Bidder to quote as per the provisions in bidding document. |
|  | 3.0 GIS Rev-5A | Annexure-5 Pg. No. 85/105 | LA parameters | Please note that for 420kV & 245kV Maharanibagh Ext GIS, supply of LA is in the GIS OEM scope. Therefore, for LA parameters, we are considering the LA parameters as per Annexure- 5 of the "3.0 GIS Rev-5A" document. Kindly confirm the same. | Confirmed. |
|  | General | _ | Surge Arrester data | Please note that all the Data regarding insulation coordination, etc, which can affect the LA parameters, shall be provided along with the NOA or within a month from the NOA for GIS LA finalization. Kindly accept the same. | Refer our reply above for LA requirement. |
|  | General | _ | Additional LA requirement or changes in LA rating | Please note that no data is provided for the Insulation co-ordination study during the tender stage, and without the study, we cannot decide the additional LA quantity requirement or changes in rating. Therefore, if any additional LA or different rating LA is required during detailed engineering, it shall be supplied by the customer without any cost implication to HYOSUNG. Kindly accept the same. | No Additional LA envisaged. |
|  | Annexure-III_Specific Requirement_Rev 10 - FINAL | ANNEXURE -13 Pg. No. 97/215 | iv. Three (3) numbers 3-phase, group-operated safety grounding switches, complete with manual and motor-driven operating mechanisms. | Please note that, as per our standard type-tested design for 245kV, we don't have a provision for ES on the Trafo side. Thus, we are providing HES instead of ES on the Trafo side for earthing duty. Thus, the revised earthing switch quantity will be as follows: Normal ES- 2 nos. HES (trafo side)- 1 nos. Kindly accept the same. | HES (High Speed Earthing Switch) in place of MES (Maintenance Earthing Switch) without any additional price implication is acceptable. |
| II | Extension of 400kV Jatikara Sub-Station |  |  |  |  |
|  | Price_schedule | Sr. No. II) 32 | 400KV GIS-ONE POLE OF 3150A CIRCUIT BREAKER WITHOUT PIR WITH INTERRUPTER, MAIN CIRCUIT, ENCLOSURE AND OPERATING MECHANISM COMPLETE IN ALL RESPECT - 2 SET | Please note that for 420kV Jhatikara Ext GIS, only Bus-sectionaliser bays are envisaged in the present scope supply. The current rating for Bus-sectionaliser bays is mentioned as 4000A in customer documents. Therefore, for the Spare requirement of the Circuit Breaker, the current rating shall be 4000A. Tentatively, we are considering 2 sets of a 4000A Circuit Breaker without PIR in our Spare parts supply. Kindly confirm the same. | Refer Amendment No-07 |
|  | Price_schedule | CT data for Bus Sectionaliser | CT data for Bus Sectionaliser | Please note that the current rating for the Bus Sectionaliser bay is 4000 A, and the CT data required for the Bus sectionaliser is not mentioned in the technical specification. So, currently, we are considering the CT data for the Bus Sectionaliser bay as per the previously executed PGCIL project. i.e. 4000-3000-2000/1 (3+2 core). The same is considered in our proposed drawings for your review. Kindly confirm the same. | Noted |
| III | Bay Extension at 400/220kV Lucknow Sub-Station |  |  |  |  |
|  | Price_schedule | Sr. No. III) 26 | Controlled Switching Device for 420 kV, 3-ph Circuit Breaker - 1 EA | Please note that, as per our understanding, CB with CSD is required for the present scope of 420kV Lucknow Ext GIS bays. However, the quantity mentioned in the BOQ does not match the requirement. A total of 2 sets (3-ph) of CSD are required, which are as follows: ICT bay- 01 Set Tie bay- 01 Set Currently, we are considering 2 Sets of CSD for the present scope of bays. Kindly confirm the same. | Refer Amendment No-07 |
|  | 420/245kV Maharanibagh Ext & 420kV Jhatikara Ext & 420/245kV Lucknow Ext | 420/245kV Maharanibagh Ext & 420kV Jhatikara Ext & 420/245kV Lucknow Ext | Shutdown requirement | We would like to inform you that the 420kV & 245kV Maharanibagh, 420kV Jhatikara, and 420kV & 245kV Lucknow GIS S/S are all extension substations. Thus, during the installation and commissioning, the adjacent existing feeder should have to take a shutdown along with one bus bar. Kindly consider the same. | Required shutdown shall be provided during the installation and commissioning. |
|  | General | _ |  | Please note that, during the installation and commissioning of extension GIS we will need to open the extension module of existing GIS to keep the existing GIS isolated while extension GIS is under HV testing. Thus, the necessary permission from the existing GIS Owner should be requested by the Client/EPC. Kindly accept the same. | Accepted |