| Sl. No. | Clause Ref. No. | Existing provision | Amended as |
| --- | --- | --- | --- |
| Volume-I (Conditions of Contract) |  |  |  |
|  | Volume-I | 400kV GIS Substation Package SS-151 (including Transformer) for (i) Extension of 400/220kV Maharani Bagh (PG) GIS S/s and 400/220/33kV, 500 MVA 3-Ph ICT at Maharani Bagh (PG) {with oil to SF6 bushing) under Augmentation of transformation capacity at 400/220kV Maharani Bagh (PG) S/s (GIS) in Delhi by 1x500 MVA, 400/220kV ICT (5th), (ii) 400kV Sectionalization bay (GIS) at 765/400kV Jhatikara (PG) S/s under Implementation of 400kV Sectionalization bay (GIS) at 765/400kV Jhatikara (PG) S/s to interconnect both 400kV sections in the event of contingency and (iii) Extension of 400/220kV Lucknow (PG) S/s under Augmentation of transformation capacity at 400/220kV Lucknow (PG) S/s by 1x500 MVA, 400/220kV ICT (3rd) along with associated bays | The Package Name “400kV GIS Substation Package SS-151 (including Transformer) for (i) Extension of 400/220kV Maharani Bagh (PG) GIS S/s and 400/220/33kV, 500 MVA 3-Ph ICT at Maharani Bagh (PG) {with oil to SF6 bushing) under Augmentation of transformation capacity at 400/220kV Maharani Bagh (PG) S/s (GIS) in Delhi by 1x500 MVA, 400/220kV ICT (5th), (ii) 400kV Sectionalization bay (GIS) at 765/400kV Jhatikara (PG) S/s under Implementation of 400kV Sectionalization bay (GIS) at 765/400kV Jhatikara (PG) S/s to interconnect both 400kV sections in the event of contingency and (iii) Extension of 400/220kV Lucknow (PG) S/s under Augmentation of transformation capacity at 400/220kV Lucknow (PG) S/s by 1x500 MVA, 400/220kV ICT (3rd) along with associated bays” stand replaced with the “400kV GIS Substation Package SS-151 for (i) Extension of 400/220kV Maharani Bagh (PG) GIS S/s under Augmentation of transformation capacity at 400/220kV Maharani Bagh (PG) S/s (GIS) in Delhi by 1x500 MVA, 400/220kV ICT (5th), (ii) 400kV Sectionalization bay (GIS) at 765/400kV Jhatikara (PG) S/s under Implementation of 400kV Sectionalization bay (GIS) at 765/400kV Jhatikara (PG) S/s to interconnect both 400kV sections in the event of contingency and (iii) Extension of 400/220kV Lucknow (PG) S/s under Augmentation of transformation capacity at 400/220kV Lucknow (PG) S/s by 1x500 MVA, 400/220kV ICT (3rd) along with associated bays”, wherever appearing in the Bidding Documents. |
|  | IFB Clause 3.1, IFB, Section-I | The scope of work covered under the subject package covers the following: Design, engineering, manufacture, testing at manufacturer’s works, supply including transportation & insurance, unloading, storage, erection, testing and commissioning at site of following equipment and items complete in all respect for: (a) Extension of 400/220kV Maharani Bagh (PG) GIS S/s and 400/220/33kV, 500 MVA 3-Ph ICT at Maharani Bagh (PG) {with oil to SF6 bushing), (b) 400kV Sectionalization bay (GIS) at 765/400kV Jhatikara (PG) S/s and (c) Extension of 400/220kV Lucknow (PG) S/s The above scope of work is indicative, and the detailed scope of work is given in the Technical Specification (Volume-II) of the Bidding Documents. | The scope of work covered under the subject package covers the following: Design, engineering, manufacture, testing at manufacturer’s works, supply including transportation & insurance, unloading, storage, erection, testing and commissioning at site of following equipment and items complete in all respect for: (a) Extension of 400/220kV Maharani Bagh (PG) GIS S/s (b) 400kV Sectionalization bay (GIS) at 765/400kV Jhatikara (PG) S/s and (c) Extension of 400/220kV Lucknow (PG) S/s The above scope of work is indicative, and the detailed scope of work is given in the Technical Specification (Volume-II) of the Bidding Documents. |
|  | ITB Clause 24.1 (b), BDS, Section-III | Supplementing ITB clause 24.1(b) with the following: The maximum losses permissible for 400/220/33kV, 500MVA 3-Phase Power Transformer offered by the bidder is stipulated in the Technical Specifications, Volume-II of the Bidding Documents. Any bid with deviations to the above shall be considered non-responsive. | Supplement para of ITB Clause 24.1 (b) in Section-III: BDS stands deleted. |
|  | ITB Clause 24.1(c), BDS, Section-III | The Time for Completion shall be as under: Description; Duration in Months from the date of Notification of Award. Taking Over by the Employer upon successful Completion of. 400kV GIS Substation Package SS-151 (including Transformer) for:. (i) Extension of 400/220kV Maharani Bagh (PG) GIS S/s and 400/220/33kV, 500 MVA 3-Ph ICT at Maharani Bagh (PG) {with oil to SF6 bushing) under Augmentation of transformation capacity at 400/220kV Maharani Bagh (PG) S/s (GIS) in Delhi by 1x500 MVA, 400/220kV ICT (5th); 20 (Twenty) Months. (ii) 400kV Sectionalization bay (GIS) at 765/400kV Jhatikara (PG) S/s under Implementation of 400kV Sectionalization bay (GIS) at 765/400kV Jhatikara (PG) S/s to interconnect both 400kV sections in the event of contingency; 14 (Fourteen) Months. (iii) Extension of 400/220kV Lucknow (PG) S/s under Augmentation of transformation capacity at 400/220kV Lucknow (PG) S/s by 1x500 MVA, 400/220kV ICT (3rd) along with associated bays.; 20 (Twenty) Months. | The Time for Completion shall be as under: Description; Duration in Months from the date of Notification of Award. Taking Over by the Employer upon successful Completion of. 400kV GIS Substation Package SS-151 for:. (i) Extension of 400/220kV Maharani Bagh (PG) GIS S/s under Augmentation of transformation capacity at 400/220kV Maharani Bagh (PG) S/s (GIS) in Delhi by 1x500 MVA, 400/220kV ICT (5th); 20 (Twenty) Months. (ii) 400kV Sectionalization bay (GIS) at 765/400kV Jhatikara (PG) S/s under Implementation of 400kV Sectionalization bay (GIS) at 765/400kV Jhatikara (PG) S/s to interconnect both 400kV sections in the event of contingency; 14 (Fourteen) Months. (iii) Extension of 400/220kV Lucknow (PG) S/s under Augmentation of transformation capacity at 400/220kV Lucknow (PG) S/s by 1x500 MVA, 400/220kV ICT (3rd) along with associated bays.; 20 (Twenty) Months. |
|  | ITB Clause 29, BDS, Section-III | Replacing ITB clause 29 29. e-Reverse Auction (e-RA) 29.1 The Employer reserves the right to conduct e-Reverse Auction (e-RA) for further reduction in the price. In case e-RA is conducted, same shall be done in the manner as indicated at Annexure-B(BDS). For the purpose of the aforesaid, the ‘Indicative Estimated Cost for e-RA’ is INR 137.04 Crore. Further, Business Rules for e-Reverse Auction and a sample format for e-Reverse Auction Notice is enclosed at Annexure-D(BDS). ……………………. ……………………….. | Replacing ITB clause 29 29. e-Reverse Auction (e-RA) 29.1 The Employer reserves the right to conduct e-Reverse Auction (e-RA) for further reduction in the price. In case e-RA is conducted, same shall be done in the manner as indicated at Annexure-B(BDS). For the purpose of the aforesaid, the ‘Indicative Estimated Cost for e-RA’ is INR 125.71 Crore. Further, Business Rules for e-Reverse Auction and a sample format for e-Reverse Auction Notice is enclosed at Annexure-D(BDS). ……………………. ……………………….. |
|  | ITB Clause 31.4, BDS, Section-III | Replace the existing provisions with the following: POWERGRID reserves the right to enter into separate contracts for different parts independent of each other covered under the subject 400kV GIS Substation Package SS-151 (including Transformer) as per the following: (i) Extension of 400/220kV Maharani Bagh (PG) GIS S/s and 400/220/33kV, 500 MVA 3-Ph ICT at Maharani Bagh (PG) {with oil to SF6 bushing) under Augmentation of transformation capacity at 400/220kV Maharani Bagh (PG) S/s (GIS) in Delhi by 1x500 MVA, 400/220kV ICT (5th),. (ii) 400kV Sectionalization bay (GIS) at 765/400kV Jhatikara (PG) S/s under Implementation of 400kV Sectionalization bay (GIS) at 765/400kV Jhatikara (PG) S/s to interconnect both 400kV sections in the event of contingency. (iii) Extension of 400/220kV Lucknow (PG) S/s under Augmentation of transformation capacity at 400/220kV Lucknow (PG) S/s by 1x500 MVA, 400/220kV ICT (3rd) along with associated bays.. Accordingly, the terms and conditions as per the bidding documents shall be applicable independently to these separate contracts. | Replace the existing provisions with the following: POWERGRID reserves the right to enter into separate contracts for different parts independent of each other covered under the subject 400kV GIS Substation Package SS-151 as per the following: (i) Extension of 400/220kV Maharani Bagh (PG) GIS S/s under Augmentation of transformation capacity at 400/220kV Maharani Bagh (PG) S/s (GIS) in Delhi by 1x500 MVA, 400/220kV ICT (5th),. (ii) 400kV Sectionalization bay (GIS) at 765/400kV Jhatikara (PG) S/s under Implementation of 400kV Sectionalization bay (GIS) at 765/400kV Jhatikara (PG) S/s to interconnect both 400kV sections in the event of contingency. (iii) Extension of 400/220kV Lucknow (PG) S/s under Augmentation of transformation capacity at 400/220kV Lucknow (PG) S/s by 1x500 MVA, 400/220kV ICT (3rd) along with associated bays.. Accordingly, the terms and conditions as per the bidding documents shall be applicable independently to these separate contracts. |
|  | Annexure-A (BDS) | Annexure-A_BDS_rev1 | Due to change in QR, the existing “Annexure-A_BDS_rev1” stands replaced with “Annexure-A_BDS_rev2”. Please also refer to Corrigendum No-02 dated **/01/2026 in this regard. |
|  | GCC Clause 1.1(ee), SCC, Section-V | The Time for Completion shall be as under: Description; Duration in Months from the date of Notification of Award. Taking Over by the Employer upon successful Completion of. 400kV GIS Substation Package SS-151 (including Transformer) for:. (i) Extension of 400/220kV Maharani Bagh (PG) GIS S/s and 400/220/33kV, 500 MVA 3-Ph ICT at Maharani Bagh (PG) {with oil to SF6 bushing) under Augmentation of transformation capacity at 400/220kV Maharani Bagh (PG) S/s (GIS) in Delhi by 1x500 MVA, 400/220kV ICT (5th); 20 (Twenty) Months. (ii) 400kV Sectionalization bay (GIS) at 765/400kV Jhatikara (PG) S/s under Implementation of 400kV Sectionalization bay (GIS) at 765/400kV Jhatikara (PG) S/s to interconnect both 400kV sections in the event of contingency; 14 (Fourteen) Months. (iii) Extension of 400/220kV Lucknow (PG) S/s under Augmentation of transformation capacity at 400/220kV Lucknow (PG) S/s by 1x500 MVA, 400/220kV ICT (3rd) along with associated bays.; 20 (Twenty) Months. | The Time for Completion shall be as under: Description; Duration in Months from the date of Notification of Award. Taking Over by the Employer upon successful Completion of. 400kV GIS Substation Package SS-151 for:. (i) Extension of 400/220kV Maharani Bagh (PG) GIS S/s under Augmentation of transformation capacity at 400/220kV Maharani Bagh (PG) S/s (GIS) in Delhi by 1x500 MVA, 400/220kV ICT (5th); 20 (Twenty) Months. (ii) 400kV Sectionalization bay (GIS) at 765/400kV Jhatikara (PG) S/s under Implementation of 400kV Sectionalization bay (GIS) at 765/400kV Jhatikara (PG) S/s to interconnect both 400kV sections in the event of contingency; 14 (Fourteen) Months. (iii) Extension of 400/220kV Lucknow (PG) S/s under Augmentation of transformation capacity at 400/220kV Lucknow (PG) S/s by 1x500 MVA, 400/220kV ICT (3rd) along with associated bays.; 20 (Twenty) Months. |
|  | GCC Clause 21.1, SCC, Section-V | Supplementing Sub-Clause GCC 21.1 The Time for Completion shall be as under: Description; Duration in Months from the date of Notification of Award. Taking Over by the Employer upon successful Completion of. 400kV GIS Substation Package SS-151 (including Transformer) for:. (i) Extension of 400/220kV Maharani Bagh (PG) GIS S/s and 400/220/33kV, 500 MVA 3-Ph ICT at Maharani Bagh (PG) {with oil to SF6 bushing) under Augmentation of transformation capacity at 400/220kV Maharani Bagh (PG) S/s (GIS) in Delhi by 1x500 MVA, 400/220kV ICT (5th); 20 (Twenty) Months. (ii) 400kV Sectionalization bay (GIS) at 765/400kV Jhatikara (PG) S/s under Implementation of 400kV Sectionalization bay (GIS) at 765/400kV Jhatikara (PG) S/s to interconnect both 400kV sections in the event of contingency; 14 (Fourteen) Months. (iii) Extension of 400/220kV Lucknow (PG) S/s under Augmentation of transformation capacity at 400/220kV Lucknow (PG) S/s by 1x500 MVA, 400/220kV ICT (3rd) along with associated bays.; 20 (Twenty) Months. | Supplementing Sub-Clause GCC 21.1 The Time for Completion shall be as under: Description; Duration in Months from the date of Notification of Award. Taking Over by the Employer upon successful Completion of. 400kV GIS Substation Package SS-151 for:. (i) Extension of 400/220kV Maharani Bagh (PG) GIS S/s under Augmentation of transformation capacity at 400/220kV Maharani Bagh (PG) S/s (GIS) in Delhi by 1x500 MVA, 400/220kV ICT (5th); 20 (Twenty) Months. (ii) 400kV Sectionalization bay (GIS) at 765/400kV Jhatikara (PG) S/s under Implementation of 400kV Sectionalization bay (GIS) at 765/400kV Jhatikara (PG) S/s to interconnect both 400kV sections in the event of contingency; 14 (Fourteen) Months. (iii) Extension of 400/220kV Lucknow (PG) S/s under Augmentation of transformation capacity at 400/220kV Lucknow (PG) S/s by 1x500 MVA, 400/220kV ICT (3rd) along with associated bays.; 20 (Twenty) Months. |
|  | GCC Clause 24.1, SCC, Section-V | Applicable for 400/220/33kV, 500MVA 3-Phase Power Transformer | Supplementing Clause GCC 24.1: Bidder shall confirm the guaranteed performance or efficiency of the equipments in response to the Technical Specifications. |
|  | GCC Clause 24.2 (b), SCC, Section-V | Supplementing Clause GCC 24.2 (b) LD for Non-Performance of the Equipment The maximum loss at rated condition (voltage, current and frequency, as applicable) for each equipment shall be corrected in accordance with IEC-60076 for the purpose of comparison of maximum losses with measured losses for levy of liquidated damages. If during factory tests, if measured loss(es) are found to be more than the specified maximum value(s), Employer at his discretion may accept or reject the equipment after assessing the liquidated damages (LD) against the contract as per rates given below and such amount shall be deducted from the contract price or otherwise recovered from Contractor. No cost benefit shall be considered in case measured losses are less than the specified maximum losses. Differential Price Factors for Liquidated Damages: The factors and the respective Indian Rupees value per unit of differential loss (applicable for each item/unit of facilities) for purpose of calculating differential price shall be as stipulated below: Sl. No.; Equipment; Parameter; Value of Liquidated Damages in Indian Rupees (applicable for each item/unit of the facilities) per unit of parameter differential with respect to maximum losses. 1.; 400/220/33kV, 500MVA 3-Phase Power Transformer; Differential Total Load Loss (KW)*; INR 8,00,000/- (Indian Rupees Eight Lakhs only) per kW. Differential I2R Loss (KW)*; INR 8,00,000/- (Indian Rupees Eight Lakhs only) per kW. Differential No Load Loss (KW); INR 10,00,000/- (Indian Rupees ten Lakhs only) per kW. Differential Auxilliary Loss (KW); INR 8,00,000/- (Indian Rupees Eight Lakhs only) per kW. Note: (*)During factory test, in case measured value of I2R Loss or Total Load Loss exceeds the specified value, then applicable Value of Liquidated damages shall be the amount of differential I2R Loss or differential Total Load Loss, whichever is higher. Also for a fraction of a kW, the penalty shall be applied on pro-rata basis. Liquidated damages shall be applied in the following manner depending on the variation of losses with respect to the maximum values: - Measured losses exceeding Guaranteed value by 0 to +2%: Rates of LD mentioned above However, the equipment shall not be accepted if either of the measured losses (i.e. Total Load Loss, I 2 R Loss, No Load Loss, Auxiliary Loss) are more than +2 percent of the Maximum losses, at rated condition, specified in Technical Specifications, Volume-II of the Bidding Documents. | Supplement para of GCC Clause 24.2 (b) in Section-V: SCC stands deleted. |
|  | 1.1, Appendix-2, Price Adjustment, Sample forms and Procedures, Section-VI | 1.1 Prices for work and materials covered under the scope of this Specification shall be furnished by the bidder in the manner specified in the Bid Form & Price Schedules. The bidder shall quote base prices for the Ex-Works price component of the equipment/materials (Transformer & Insulating Oil, CB, CT, CVT, ISO, SA, PVC/XLPE insulated Power & Control Cables, as applicable), the complete equipment procured as spares (Transformers, CB, CT, CVT, ISO, SA, PVC/XLPE insulated Power & Control Cables, as applicable), Substation Structures and installation (including civil works) price component of the equipment/materials. These price components for certain equipment/ materials, as specified, shall be subject to price adjustment to reflect changes in the cost of labour and material components as per the provisions given below: | 1.1 Prices for work and materials covered under the scope of this Specification shall be furnished by the bidder in the manner specified in the Bid Form & Price Schedules. The bidder shall quote base prices for the Ex-Works price component of the equipment/materials (CB, CT, CVT, ISO, SA, PVC/XLPE insulated Power & Control Cables, as applicable), the complete equipment procured as spares (CB, CT, CVT, ISO, SA, PVC/XLPE insulated Power & Control Cables, as applicable), Substation Structures and installation (including civil works) price component of the equipment/materials. These price components for certain equipment/ materials, as specified, shall be subject to price adjustment to reflect changes in the cost of labour and material components as per the provisions given below: |
|  | 2.0 (D) & 2.0 (E), Appendix-2, Price Adjustment, Sample forms and Procedures, Section-VI | 2.0 Ex-works Price Component The formulae for calculating the price adjustment to be applied to the Ex-works price component of the equipment/material will be as follows: …………………. D. Price adjustment formula for Ex-works Price component of Transformer (excluding Insulating Oil) (ratings above 10MVA or voltage above 33kV up to 400kV) The formula for calculating the price adjustment to be applied to the Ex-works price component of the main equipment for Transformer will be as follows: P1 = P0 x {0.15+ ax(A1/A0) + bx(B1/B0) + cx(C1/C0) + dx(D1/D0) + l x(L1/L0)} – P0 Where, P1 = Price adjustment amount, expressed in currency of bid, payable to Contractor, for each shipment (if it works out negative, that would mean the amount to be recovered by the Employer from the Contractor). P0 = Ex-works price component of main equipment for Transformer (without Insulating oil), in the currency of bid, shipment-wise. a = Co-efficient of Copper, Value of which shall be between 0.27 & 0.33. b = Co-efficient of Electrical Lamination Steel, Value of which shall be between 0.25 & 0.31. c = Co-efficient of Construction Steel, Value of which shall be between 0.06 & 0.08. d = Co-efficient of Insulating material, Value of which shall be between 0.05 & 0.06. l = Co-efficient of Labour, Value of which shall be between 0.14 & 0.17. and the sum of a, b, c, d & l shall be 0.85. A = Price indices for copper wire rod, as published by IEEMA. B = Price indices for CRGO Electrical Steel Lamination, as published by IEEMA. C = Price indices for average price of Steel Plates (10mm thick), as published by IEEMA D = Price indices for Insulating materials, as published by IEEMA. L = Indian field labour index – namely All India average consumer price index for Industrial Workers (monthly) (Base: 2016= 100), as published by Labour Bureau, Shimla, Government of India (http://labourbureaunew.gov.in). E. For Insulating Oil for Transformer P2 = P0 x {0.15+ 0.85 x (E1/E0) } – P0 P2 = Price adjustment amount for insulating oil for Transformer, expressed in currency of bid, payable to Contractor, for each shipment (if it works out negative, that would mean the amount to be recovered by the Employer from the Contractor). P0 = Ex-works price of insulating oil for Transformer in the currency of bid, shipment-wise. E = Published recognized price indices for Insulating oil. 2.1 For Transformer (excluding Insulating Oil) (ratings above 10MVA or voltage above 33kV up to 400kV) and Insulating Oil: i) Subscript '0' refers to indices as on thirty (30) days prior to date of opening of Bids, for materials, oil & ninety (90) days prior to date of opening of Bids for labour. ii) Subscript ‘1’ refers to indices as on thirty (30) days prior to date of shipment, for materials, oil & ninety (90) days prior to date of shipment, for labour. 2.2 The price adjustment for the Ex-Works price component for Transformer (excluding Insulating Oil) (ratings above 10MVA or voltage above 33kV up to 400kV) and Insulating Oil for each shipment will not be subject to any ceiling. | Clauses 2.0 (D) and 2.0 (E) of Appendix-2, stand deleted. |
|  | Appendix-4, Sample forms and Procedures, Section-VI | Appendix-4 TIME SCHEDULE - The Project Completion Schedule shall be as follows: Description; Duration in Months from the date of Notification of Award. Taking Over by the Employer upon successful Completion of. 400kV GIS Substation Package SS-151 (including Transformer) for:. (i) Extension of 400/220kV Maharani Bagh (PG) GIS S/s and 400/220/33kV, 500 MVA 3-Ph ICT at Maharani Bagh (PG) {with oil to SF6 bushing) under Augmentation of transformation capacity at 400/220kV Maharani Bagh (PG) S/s (GIS) in Delhi by 1x500 MVA, 400/220kV ICT (5th); 20 (Twenty) Months. (ii) 400kV Sectionalization bay (GIS) at 765/400kV Jhatikara (PG) S/s under Implementation of 400kV Sectionalization bay (GIS) at 765/400kV Jhatikara (PG) S/s to interconnect both 400kV sections in the event of contingency; 14 (Fourteen) Months. (iii) Extension of 400/220kV Lucknow (PG) S/s under Augmentation of transformation capacity at 400/220kV Lucknow (PG) S/s by 1x500 MVA, 400/220kV ICT (3rd) along with associated bays.; 20 (Twenty) Months. | Appendix-4 TIME SCHEDULE - The Project Completion Schedule shall be as follows: Description; Duration in Months from the date of Notification of Award. Taking Over by the Employer upon successful Completion of. 400kV GIS Substation Package SS-151 for:. (i) Extension of 400/220kV Maharani Bagh (PG) GIS S/s under Augmentation of transformation capacity at 400/220kV Maharani Bagh (PG) S/s (GIS) in Delhi by 1x500 MVA, 400/220kV ICT (5th); 20 (Twenty) Months. (ii) 400kV Sectionalization bay (GIS) at 765/400kV Jhatikara (PG) S/s under Implementation of 400kV Sectionalization bay (GIS) at 765/400kV Jhatikara (PG) S/s to interconnect both 400kV sections in the event of contingency; 14 (Fourteen) Months. (iii) Extension of 400/220kV Lucknow (PG) S/s under Augmentation of transformation capacity at 400/220kV Lucknow (PG) S/s by 1x500 MVA, 400/220kV ICT (3rd) along with associated bays.; 20 (Twenty) Months. |
|  | Appendix-8, Sample forms and Procedures, Section-VI | Appendix-8 GUARANTEES, LIQUIDATED DAMAGES FOR NON PERFORMANCE 1.0 The equipment offered shall meet the rating and performance requirements stipulated in Technical Specification for various equipment. 2.0 In particular, 400/220/33kV, 500MVA 3-Phase Power Transformer offered under this contract shall meet the maximum loss requirement as stipulated in Technical Specifications. - If the aforementioned guarantees are not established at factory tests, then the Employer at his discretion may reject or accept the equipment after assessing the liquidated damages as follows against the Contract: Sl. No.; Equipment; Parameter; Value of Liquidated Damages in Indian Rupees (applicable for each item/unit of the facilities) per unit of parameter differential with respect to maximum losses. 1.; 400/220/33kV, 500MVA 3-Phase Power Transformer; Differential Total Load Loss (KW)*; INR 8,00,000/- (Indian Rupees Eight Lakhs only) per kW. Differential I2R Loss (KW)*; INR 8,00,000/- (Indian Rupees Eight Lakhs only) per kW. Differential No Load Loss (KW); INR 10,00,000/- (Indian Rupees ten Lakhs only) per kW. Differential Auxilliary Loss (KW); INR 8,00,000/- (Indian Rupees Eight Lakhs only) per kW. Note: (*) During factory test, in case measured value of I2R Loss or Total Load Loss exceeds the specified value, then applicable Value of Liquidated damages shall be the amount of differential I2R Loss or differential Total Load Loss, whichever is higher. Also for a fraction of a kW, the penalty shall be applied on pro-rata basis. 3.0 Liquidated damages shall be applied in the following manner depending on the variation of losses with respect to the maximum values: - Measured losses exceeding Guaranteed value by 0 to +2%: Rates of LD mentioned above Such amounts shall be deducted from the Contract Price or otherwise recovered from the Contractor. However, the equipment shall not be accepted if either of the measured losses (i.e. Total Load Loss, I2R Loss, No Load Loss, Auxiliary Loss) are more than +2 percent of the Maximum losses, at rated condition, specified in Technical Specifications, Volume-II of the Bidding Documents. | Appendix-8 GUARANTEES, LIQUIDATED DAMAGES FOR NON PERFORMANCE NOT APPLICABLE |
| Volume-II: Technical Specifications |  |  |  |
|  | Section Project/ 2.1.A.3 | 3. 400/220 kV, 500 MVA Autotransformer. - One number, 400/220/33kV, 500 MVA, 3-Phase Auto Transformer along with all Fittings, accessories, marshalling box including all materials. - DIGITAL RTCC Panel: RTCC Panel is to be supply with 6 nos. digital RTCC relay (one each for four numbers 3-Ph existing ICT, one for ICT under present scope and one Spare). Existing three numbers of 3-phase ICT are with conventional type of RTCC panel, which are to be dismantled and same is to be handed over to POWERGRID. Installation of above mentioned Digital RTCC panel, also include scope of dismantling existing RTCC panels. Necessary re-wiring, cabling is also under present scope of work. - 400/220/33kV, 3-ph Autotransformer shall be suitable for connecting both HV side (400kV) with GIS SF6/Oil Interface, as per IEC-62271-211 and & IV side (220kV) with Cable/Oil Interface. The LV side (33kV) of 400/220/33kV Transformer shall have conventional AIS type termination. | 3. 400/220 kV, 500 MVA Autotransformer (Owner Supplied). - Deleted. - DIGITAL RTCC Panels with 06 Nos. of relays for 400/220kV Auto Transformers: Existing 3 Nos. of 400/220kV 3-ph autotransformers at Maharani Bagh substation are commissioned with parallel operation using Analogue RTCC Panels. The RTCC panels under present scope shall comprise of 06 Nos. of Digital RTCC Relays {Three (3) for existing transformers, One (1) for present scope transformer & Two (2) nos. as spare}. The Present Scope shall include required cabling between existing transformer RTCC panels/OLTC MB/Transformer MB and the Digital RTCC panels, wiring modifications in existing panels as per RTCC scheme requirement, dismantling of existing RTCC panels if required etc so as to enable parallel operation of transformer under present scope with existing transformers through Digital RTCC relays. - Deleted. |
|  | Section Project/ 2.1.A.5 | Substation Automation System Augmentation of Substation Automation System for bays as per BPS (bay as defined in technical specification. ….. ………… …. However, no work is envisaged at remote end (SLDC/RLDC/RTAMC/NTAMC) under the present scope. | Substation Automation System Augmentation of Substation Automation System for bays as per BPS (bay as defined in technical specification. ….. ………… …. However, no work is envisaged at remote end (SLDC/RLDC/RTAMC/NTAMC) under the present scope. Integration of Digital RTCC relays for 400/220kV Transformers [existing and transformer being supplied under present scope] with substation automation system is also included under present scope. Integration of Online insulating oil drying system based on IEC-61850 for 400/220kV Transformers (supplied under present scope through separate package) with SAS along with associated Ethernet switch, LIU patch cords etc. is under present scope. |
|  | Section Project/ 2.3.A.4 | 400/220 kV, 500 MVA Autotransformer (Owner Supplied). Supply, erection, testing and commissioning of 400/220 kV, 500 MVA Autotransformer is covered under separate package. However, following associated works are covered under the scope of this package: - Civil works for 400/220kV Auto-Transformer foundation complete in all respect, firewalls, earthing connection to main earth mat and earth pits etc. (as required) as per technical specification. - Overhead connection of HV, IV & LV bushings of (400/220kV) Autotransformers to substation equipment’s. - Supply, laying and termination of cables along with associated accessories from marshaling box of 400/220/33kV Autotransformer to BMK/Switchyard Panel Rooms/Control Room/ auxiliary Building as per requirement. DIGITAL RTCC Panel: RTCC Panel is to be supply with 4 nos. digital RTCC relay (one each for Two numbers 3-Ph existing ICT, one for ICT under present scope and one Spare). Existing three numbers of 3-phase ICT are with conventional type of RTCC panel, which are to be dismantled and same is to be handed over to POWERGRID. Installation of above mentioned Digital RTCC panel, also include scope of dismantling existing RTCC panels. Necessary re-wiring, cabling is also under present scope of work. | 400/220 kV, 500 MVA Autotransformer (Owner Supplied). Supply, erection, testing and commissioning of 400/220 kV, 500 MVA Autotransformer is covered under separate package. However, following associated works are covered under the scope of this package: - Civil works for 400/220kV Auto-Transformer foundation complete in all respect, firewalls, earthing connection to main earth mat and earth pits etc. (as required) as per technical specification. - Overhead connection of HV, IV & LV bushings of (400/220kV) Autotransformers to substation equipment’s. - Supply, laying and termination of cables along with associated accessories from marshaling box of 400/220/33kV Autotransformer to BMK/Switchyard Panel Rooms/Control Room/ auxiliary Building as per requirement. DIGITAL RTCC Panels with 04 Nos. of relays for 400/220kV Auto Transformers: Existing 2 Nos. of 400/220kV 3-ph autotransformers at Lucknow substation are commissioned with parallel operation using Analogue RTCC Panels. The RTCC panels under present scope shall comprise of 04 Nos. of Digital RTCC Relays {Two (2) for existing transformers, One (1) for present scope transformer & One (1) no. as spare}. The Present Scope shall include required cabling between existing transformer RTCC panels/OLTC MB/Transformer MB and the Digital RTCC panels, wiring modifications in existing panels as per RTCC scheme requirement, dismantling of existing RTCC panels if required etc so as to enable parallel operation of transformer under present scope with existing transformers through Digital RTCC relays. |
|  | Section Project/ 2.3.A.6 | Substation Automation System The Existing 400/220 kV Lucknow Substation is a conventional Substation (Control Panel). ….. ………… XIII. ……….. XIV. ………….which shall be further engineered by the bidder.” | Substation Automation System The Existing 400/220 kV Lucknow Substation is a conventional Substation (Control Panel). ….. ………… XIII. ……….. XIV. ………….which shall be further engineered by the bidder.” XV. Integration of Digital RTCC relays for 400/220kV Transformers [existing and transformer being supplied under present scope] with substation automation system is also included under present scope. XVI. Integration of Online insulating oil drying system based on IEC-61850 for 400/220kV Transformers (supplied under present scope through separate package) with SAS along with associated Ethernet switch, LIU patch cords etc. is under present scope. |
|  | 3.0, Specific Exclusion, Section Project | 3. SPECIFIC EXCLUSION The following items of work are specifically excluded from the scope of the specification: - Employer’s site office - Approach road to Substation - 400/220 kV, 500 MVA Autotransformer for Lucknow Substation | 3. SPECIFIC EXCLUSION The following items of work are specifically excluded from the scope of the specification: - Employer’s site office - Approach road to Substation - 400/220 kV, 500 MVA Autotransformer for Lucknow Substation - Supply, Erection, Testing & Commissioning of 400/220 kV, 500 MVA Autotransformer for Maharani Bagh Substation Cable from 400kV Transformer to MB of Transformer. |
| Volume-III: Bid forms & Price Schedules |  |  |  |
|  | First Envelope and Bid Forms | First Envelope and Bid Forms_rev2 | Due to changes in Attachment-9 and Attachment-12 as per above Amendment, the existing ‘First Envelope and Bid Forms_rev2’’ excel stand revised as ‘First Envelope and Bid Forms_rev3’ and is attached herewith. Note- Bidders are requested to consider the revised excel ‘First Envelope and Bid Forms_rev3’ for bid preparation/submission. It may be noted that while submitting the bid, Bidders are required to change the excel file name from ‘First Envelope and Bid Forms_rev3’ to ‘First Envelope and Bid Forms’. As per the provisions of the portal, it is mandatory to upload the excel file titled ‘First Envelope and Bid Forms’ (Bidders may refer user manuals at the portal https://etender.powergrid.in regarding submission of bid). |
|  | Attachment-3 (QR) to First Envelope Bid Form | The existing File ‘Attachment-3 (QR)_rev1’ MS Excel File stands replaced with ‘Attachment-3 (QR)_rev2’ |  |
|  | Attachments to the Bid Form | 400kV GIS Substation Package SS-151 (including Transformer) for (i) Extension of 400/220kV Maharani Bagh (PG) GIS S/s and 400/220/33kV, 500 MVA 3-Ph ICT at Maharani Bagh (PG) {with oil to SF6 bushing) under Augmentation of transformation capacity at 400/220kV Maharani Bagh (PG) S/s (GIS) in Delhi by 1x500 MVA, 400/220kV ICT (5th), (ii) 400kV Sectionalization bay (GIS) at 765/400kV Jhatikara (PG) S/s under Implementation of 400kV Sectionalization bay (GIS) at 765/400kV Jhatikara (PG) S/s to interconnect both 400kV sections in the event of contingency and (iii) Extension of 400/220kV Lucknow (PG) S/s under Augmentation of transformation capacity at 400/220kV Lucknow (PG) S/s by 1x500 MVA, 400/220kV ICT (3rd) along with associated bays | The Package Name, wherever appeared in the Attachments to the Bid Form “400kV GIS Substation Package SS-151 (including Transformer) for (i) Extension of 400/220kV Maharani Bagh (PG) GIS S/s and 400/220/33kV, 500 MVA 3-Ph ICT at Maharani Bagh (PG) {with oil to SF6 bushing) under Augmentation of transformation capacity at 400/220kV Maharani Bagh (PG) S/s (GIS) in Delhi by 1x500 MVA, 400/220kV ICT (5th), (ii) 400kV Sectionalization bay (GIS) at 765/400kV Jhatikara (PG) S/s under Implementation of 400kV Sectionalization bay (GIS) at 765/400kV Jhatikara (PG) S/s to interconnect both 400kV sections in the event of contingency and (iii) Extension of 400/220kV Lucknow (PG) S/s under Augmentation of transformation capacity at 400/220kV Lucknow (PG) S/s by 1x500 MVA, 400/220kV ICT (3rd) along with associated bays” Stands replaced with “400kV GIS Substation Package SS-151 for (i) Extension of 400/220kV Maharani Bagh (PG) GIS S/s under Augmentation of transformation capacity at 400/220kV Maharani Bagh (PG) S/s (GIS) in Delhi by 1x500 MVA, 400/220kV ICT (5th), (ii) 400kV Sectionalization bay (GIS) at 765/400kV Jhatikara (PG) S/s under Implementation of 400kV Sectionalization bay (GIS) at 765/400kV Jhatikara (PG) S/s to interconnect both 400kV sections in the event of contingency and (iii) Extension of 400/220kV Lucknow (PG) S/s under Augmentation of transformation capacity at 400/220kV Lucknow (PG) S/s by 1x500 MVA, 400/220kV ICT (3rd) along with associated bays”. |
|  | Schedul-1& 2, ICT-5 Maharani Bagh, Price Schedule | S. No; Material Code; Description; Unit; Qty. I; ICT-5 Maharani Bagh. 1; 1000004798; 500MVA, 400KV/220/33 KV, 3-phase Autotransformer excluding insulating oil; EA; 1. 2; 1000013986; Insulating Oil for 500MVA, 400KV/220/33 KV, 3-phase Autotransformer; SET; 1. 45; 1000060011; 420KV,1250A OIL TO SF6 BUSHING WITH METAL PARTS AND GASKETS; EA; 1. 46; 1000030937; 52KV, 3150A RIP BUSHING WITH METAL PARTS AND GASKETS; EA; 1. 47; 1000002071; 36kV, 2000A Bushing with metal parts and gaskets for Transformer; EA; 1. 48; 1000016676; Oil cooler pump with motor for 400kV Transformer; SET; 1. 49; 1000009731; Cooler fan with motor for 400kV Transformer; EA; 1. 50; 1000028774; Local winding temperature indicator (WTI) with contact; EA; 1. 51; 1000026245; OTI complete with contacts & sensing device; SET; 1. 52; 1000016694; Oil flow indicator for 400kV T/F with flow switch; SET; 1. 53; 1000007922; Buchholz Relay (Main Tank) complete with float and contacts for Transformer; SET; 1. 54; 1000028280; Magnetic Oil Level Gauge; EA; 1. 55; 1000009586; Starters, contactors, switches and relays for electrical control panels of 400kV T/F (one set of each type); SET; 1. 56; 1000032089; SPARES INSULATING OIL TO BE HANDED OVER TO OWNER AFTER COMMISSIONING; KL; 5. 57; 1000076494; 245KV,2150A OIL TO OIL TYPE, RIP BUSHING; EA; 1. 85; 1000058328; 400KV GIS- SINGLE PHASE VT WITH ASSOCIATED ENCLOSURE COMPLETE IN ALLRESPECT; EA; 1. 115; 1000058296; 220KV GIS- SINGLE PHASE VT WITH ASSOCIATED ENCLOSURE COMPLETE IN ALLRESPECT; EA; 2. 116; 1000058304; 220KV GIS- SURGE COUNTER/ MONITOR; EA; 1. | S. No; Material Code; Description; Unit; Qty. I; ICT-5 Maharani Bagh. 1; 1000004798; 500MVA, 400KV/220/33 KV, 3-phase Autotransformer excluding insulating oil; EA; 0. 2; 1000013986; Insulating Oil for 500MVA, 400KV/220/33 KV, 3-phase Autotransformer; SET; 0. 45; 1000060011; 420KV,1250A OIL TO SF6 BUSHING WITH METAL PARTS AND GASKETS; EA; 0. 46; 1000030937; 52KV, 3150A RIP BUSHING WITH METAL PARTS AND GASKETS; EA; 0. 47; 1000002071; 36kV, 2000A Bushing with metal parts and gaskets for Transformer; EA; 0. 48; 1000016676; Oil cooler pump with motor for 400kV Transformer; SET; 0. 49; 1000009731; Cooler fan with motor for 400kV Transformer; EA; 0. 50; 1000028774; Local winding temperature indicator (WTI) with contact; EA; 0. 51; 1000026245; OTI complete with contacts & sensing device; SET; 0. 52; 1000016694; Oil flow indicator for 400kV T/F with flow switch; SET; 0. 53; 1000007922; Buchholz Relay (Main Tank) complete with float and contacts for Transformer; SET; 0. 54; 1000028280; Magnetic Oil Level Gauge; EA; 0. 55; 1000009586; Starters, contactors, switches and relays for electrical control panels of 400kV T/F (one set of each type); SET; 0. 56; 1000032089; SPARES INSULATING OIL TO BE HANDED OVER TO OWNER AFTER COMMISSIONING; KL; 0. 57; 1000076494; 245KV,2150A OIL TO OIL TYPE, RIP BUSHING; EA; 0. 85; 1000058328; 400KV GIS- SINGLE PHASE VT WITH ASSOCIATED ENCLOSURE COMPLETE IN ALLRESPECT; EA; 0. 115; 1000058296; 220KV GIS- SINGLE PHASE VT WITH ASSOCIATED ENCLOSURE COMPLETE IN ALLRESPECT; EA; 0. 116; 1000058304; 220KV GIS- SURGE COUNTER/ MONITOR; EA; 0. |
|  | Schedul-1& 2, Bus Sec Bay Jhatikara, Price Schedule | S. No; Material Code; Description; Unit; Qty. II; Bus Sec Bay Jhatikara. 41; 1000058310; 400KV GIS - SINGLE PHASE FAST EARTHING SWITCH INCLUDING MAIN CIRCUIT,ENCLOSURE, DRIVING MECHANISM AND SUPPORT INSULATOR ETC., COMPLETE INALL RESPECT (NOTE 1 - IN CASE, DIS-CONNECTOR SWITCH (DS) & EARTHSWITCH (ES) IS PROVIDED IN A SAME ENCLOSURE WITH COMMON OPERATINGMECHANISM, THEN THE MODULE COMPRISING OF DIS-CONNECTOR & EARTH SWITCHIN SINGLE ENCLOSURE WITH COMMON OPERATING MECHANISM IS TO BE PROVIDEDUNDER THE HEAD OF SPARE DIS-CONNECTOR ONLY. NOTE 2 - IN CASE, DIS-CONNECTOR SWITCH (DS) & EARTH SWITCH (ES) IS PROVIDED IN A SAMEENCLOSURE WITH SEPARATE OPERATING MECHANISM, THEN THE MODULECOMPRISING OF DIS-CONNECTOR & EARTH SWITCH IN SINGLE ENCLOSURE WITHSEPARATE OPERATING MECHANISM IS TO BE PROVIDED UNDER THE HEAD OF SPAREDIS-CONNECTOR ONLY.); EA; 1. 43; 1000058308; OPEN/CLOSE CONTACTOR ASSEMBLY, TIMERS, KEY INTERLOCK, INTERLOCKING COILS, RELAYS, PUSH BUTTONS, INDICATING LAMPS, POWER CONTACTORS, RESISTORS, FUSES, MCBS & DRIVE CONTROL CARDS ETC. (AS APPLICABLE) ONEOF EACH TYPE FOR ONE COMPLETE MOM BOX FOR 400KV GIS FAST EARTHINGSWITCH; SET; 1. 46; 1000049777; LIMIT SWITCHES AND AUX. SWITCHES FOR ONE COMPLETE MOM BOX FOR FAST EARTHING SWITCH (IF APPLICABLE)-400KV GIS; SET; 2. 49; 1000058309; DRIVE MECHANISM FOR 400KV GIS FAST EARTHING SWITCH; SET; 1. 51; 1000058311; MOTOR FOR DRIVE MECHANISM FOR 400KV GIS FAST EARTHING SWITCH; EA; 1. | S. No; Material Code; Description; Unit; Qty. II; Bus Sec Bay Jhatikara. 41; 1000058310; 400KV GIS - SINGLE PHASE FAST EARTHING SWITCH INCLUDING MAIN CIRCUIT,ENCLOSURE, DRIVING MECHANISM AND SUPPORT INSULATOR ETC., COMPLETE INALL RESPECT (NOTE 1 - IN CASE, DIS-CONNECTOR SWITCH (DS) & EARTHSWITCH (ES) IS PROVIDED IN A SAME ENCLOSURE WITH COMMON OPERATINGMECHANISM, THEN THE MODULE COMPRISING OF DIS-CONNECTOR & EARTH SWITCHIN SINGLE ENCLOSURE WITH COMMON OPERATING MECHANISM IS TO BE PROVIDEDUNDER THE HEAD OF SPARE DIS-CONNECTOR ONLY. NOTE 2 - IN CASE, DIS-CONNECTOR SWITCH (DS) & EARTH SWITCH (ES) IS PROVIDED IN A SAMEENCLOSURE WITH SEPARATE OPERATING MECHANISM, THEN THE MODULECOMPRISING OF DIS-CONNECTOR & EARTH SWITCH IN SINGLE ENCLOSURE WITHSEPARATE OPERATING MECHANISM IS TO BE PROVIDED UNDER THE HEAD OF SPAREDIS-CONNECTOR ONLY.); EA; 0. 43; 1000058308; OPEN/CLOSE CONTACTOR ASSEMBLY, TIMERS, KEY INTERLOCK, INTERLOCKINGCOILS, RELAYS, PUSH BUTTONS, INDICATING LAMPS, POWER CONTACTORS, RESISTORS, FUSES, MCBS & DRIVE CONTROL CARDS ETC. (AS APPLICABLE) ONEOF EACH TYPE FOR ONE COMPLETE MOM BOX FOR 400KV GIS FAST EARTHINGSWITCH; SET; 0. 46; 1000049777; LIMIT SWITCHES AND AUX. SWITCHES FOR ONE COMPLETE MOM BOX FOR FASTEARTHING SWITCH (IF APPLICABLE)-400KV GIS; SET; 0. 49; 1000058309; DRIVE MECHANISM FOR 400KV GIS FAST EARTHING SWITCH; SET; 0. 51; 1000058311; MOTOR FOR DRIVE MECHANISM FOR 400KV GIS FAST EARTHING SWITCH; EA; 0. |
|  | Schedul-1& 2, ICT Bay 400/220kV Lucknow SS, Price Schedule | S. No; Material Code; Description; Unit; Qty. III; ICT Bay 400/220kV Lucknow SS. 68; 1000049777; LIMIT SWITCHES AND AUX. SWITCHES FOR ONE COMPLETE MOM BOX FOR FASTEARTHING SWITCH (IF APPLICABLE)-400KV GIS; SET; 2. 73; 1000058308; OPEN/CLOSE CONTACTOR ASSEMBLY, TIMERS, KEY INTERLOCK, INTERLOCKINGCOILS, RELAYS, PUSH BUTTONS, INDICATING LAMPS, POWER CONTACTORS, RESISTORS, FUSES, MCBS & DRIVE CONTROL CARDS ETC. (AS APPLICABLE) ONE OF EACH TYPE FOR ONE COMPLETE MOM BOX FOR 400KV GIS FAST EARTHING SWITCH; SET; 1. 74; 1000058309; DRIVE MECHANISM FOR 400KV GIS FAST EARTHING SWITCH; SET; 1. 75; 1000058310; 400KV GIS - SINGLE PHASE FAST EARTHING SWITCH INCLUDING MAIN CIRCUIT,ENCLOSURE, DRIVING MECHANISM AND SUPPORT INSULATOR ETC., COMPLETE INALL RESPECT (NOTE 1 - IN CASE, DIS-CONNECTOR SWITCH (DS) & EARTHSWITCH (ES) IS PROVIDED IN A SAME ENCLOSURE WITH COMMON OPERATING MECHANISM, THEN THE MODULE COMPRISING OF DIS-CONNECTOR & EARTH SWITCHIN SINGLE ENCLOSURE WITH COMMON OPERATING MECHANISM IS TO BE PROVIDEDUNDER THE HEAD OF SPARE DIS-CONNECTOR ONLY. NOTE 2 - IN CASE, DIS-CONNECTOR SWITCH (DS) & EARTH SWITCH (ES) IS PROVIDED IN A SAMEENCLOSURE WITH SEPARATE OPERATING MECHANISM, THEN THE MODULE COMPRISING OF DIS-CONNECTOR & EARTH SWITCH IN SINGLE ENCLOSURE WITHSEPARATE OPERATING MECHANISM IS TO BE PROVIDED UNDER THE HEAD OF SPAREDIS-CONNECTOR ONLY.); EA; 1. 76; 1000058311; MOTOR FOR DRIVE MECHANISM FOR 400KV GIS FAST EARTHING SWITCH; EA; 1. | S. No; Material Code; Description; Unit; Qty. III; ICT Bay 400/220kV Lucknow SS. 68; 1000049777; LIMIT SWITCHES AND AUX. SWITCHES FOR ONE COMPLETE MOM BOX FOR FASTEARTHING SWITCH (IF APPLICABLE)-400KV GIS; SET; 0. 73; 1000058308; OPEN/CLOSE CONTACTOR ASSEMBLY, TIMERS, KEY INTERLOCK, INTERLOCKING COILS, RELAYS, PUSH BUTTONS, INDICATING LAMPS, POWER CONTACTORS, RESISTORS, FUSES, MCBS & DRIVE CONTROL CARDS ETC. (AS APPLICABLE) ONE OF EACH TYPE FOR ONE COMPLETE MOM BOX FOR 400KV GIS FAST EARTHING SWITCH; SET; 0. 74; 1000058309; DRIVE MECHANISM FOR 400KV GIS FAST EARTHING SWITCH; SET; 0. 75; 1000058310; 400KV GIS - SINGLE PHASE FAST EARTHING SWITCH INCLUDING MAIN CIRCUIT,ENCLOSURE, DRIVING MECHANISM AND SUPPORT INSULATOR ETC., COMPLETE INALL RESPECT (NOTE 1 - IN CASE, DIS-CONNECTOR SWITCH (DS) & EARTHSWITCH (ES) IS PROVIDED IN A SAME ENCLOSURE WITH COMMON OPERATING MECHANISM, THEN THE MODULE COMPRISING OF DIS-CONNECTOR & EARTH SWITCHIN SINGLE ENCLOSURE WITH COMMON OPERATING MECHANISM IS TO BE PROVIDEDUNDER THE HEAD OF SPARE DIS-CONNECTOR ONLY. NOTE 2 - IN CASE, DIS-CONNECTOR SWITCH (DS) & EARTH SWITCH (ES) IS PROVIDED IN A SAME ENCLOSURE WITH SEPARATE OPERATING MECHANISM, THEN THE MODULE COMPRISING OF DIS-CONNECTOR & EARTH SWITCH IN SINGLE ENCLOSURE WITH SEPARATE OPERATING MECHANISM IS TO BE PROVIDED UNDER THE HEAD OF SPAREDIS-CONNECTOR ONLY.); EA; 0. 76; 1000058311; MOTOR FOR DRIVE MECHANISM FOR 400KV GIS FAST EARTHING SWITCH; EA; 0. |
|  | Schedul-3, ICT-5 Maharani Bagh, Price Schedule | S. No; Service Code; Description; Unit; Qty. I; ICT-5 Maharani Bagh. 1; 100000015; 500MVA, 400KV/220/33 KV, 3-phase Autotransformer excluding insulating oil; EA; 1. 2; 100001910; Insulating Oil for 500MVA, 400KV/220/33 KV, 3-phase Autotransformer; SET; 1. | S. No; Service Code; Description; Unit; Qty. I; ICT-5 Maharani Bagh. 1; 100000015; 500MVA, 400KV/220/33 KV, 3-phase Autotransformer excluding insulating oil; EA; 0. 2; 100001910; Insulating Oil for 500MVA, 400KV/220/33 KV, 3-phase Autotransformer; SET; 0. |
|  | Price Schedule | In view of the above amendment, the existing file “Price schedule_rev2” stands replaced with “Price_schedule_rev3” and is attached herewith this Amendment. Note: Bidders are requested to consider the revised excel file “Price_schedule_rev3” for bid preparation/submission. It may be noted that while submitting the bid, bidders are requested to keep the excel file name as “Price_schedule_rev3”. (Bidders may refer user manuals at the portal https://etender.powergrid.in regarding submission of bid). |  |