| Sl. No. | # Tender Clause | # Bidder’s Query | # POWERGRID Reply |
| --- | --- | --- | --- |
| Volume-II: Technical Specifications |  |  |  |
|  | - | Kindly provide the existing Hyosung Make 220kV bus bar extension model drawings. | Details shall be shared during detail engineering. |
|  | Extension of 400/220kV Maharani Bagh (PG) GIS S/s under Augmentation of transformation capacity at 400/220kV Maharani Bagh (PG) S/s (GIS) in Delhi by 1x500 MVA, 400/220kV ICT (5th) | Maharani Bagh existing busbar is of M/s Hitachi make. Details of existing busbar relay required to arrange quote. | The make and model of existing bus bar relay is indicated at clause 2.1.A.4 of Section project Bidder is requested to refer the same. |
|  |  | Maharani Bagh existing busbar is of M/s Hitachi make. Please provide details of existing busbar relay. |  |
|  | Extension of 400/220kV Lucknow (PG) S/s under Augmentation of transformation capacity at 400/220kV Lucknow (PG) S/s by 1x500 MVA, 400/220kV ICT (3rd) along with associated bays. | Lucknow s/s - As per section project, existing RTU to be replaced with new BCU’s. Our scope is limited to supply of required Loose BCU’s as per I/O’s mentioned in section project. Retrofitting of new BCU’s in exiting RTU panel, cable identification/termination is not in our scope. Required inputs for engineering (i.e. existing cable schedule, list of signals) to be provided by Vendor. | Bidder to quote as per the provisions in bidding document. However for SUBSTATION AUTOMATION SYSTEM (SAS) scope kindly refer clause 2.3.A.6 of section project. |
|  |  | Lucknow s/s - As per section project, existing RTU to be replaced with new BCU’s. Please provide existing RTU drawings and signal list for confirming BCU count and RTU panel. Only 61850 compatible IED’s can be integrated to upgraded SAS. Please confirm. |  |
|  |  | Only 61850 compatible IED’s can be integrated to upgraded SAS. | Integration of following IEDs in New SAS is envisaged as per TS. 1. Existing IEDs which are already IEC 61850 compliant. 2. Existing IEDs which are required to be upgraded to IEC 61850 compliant (by POWERGRID). 3. IEDs to be supplied under the present scope. |
|  | Necessary up-gradation of firmware of IEDs if required shall be deemed to be included elsewhere. Software for the configuration tool of IEDs shall be handed over by the vendor after execution of the contract. | Necessary up-gradation of firmware of IEDs if required shall be deemed to be included elsewhere. Software for the configuration tool of IEDs shall be handed over by the vendor after execution of the contract. This cannot be taken up as most of the existing IED’s are on proprietary protocol. | Bidder to quote as per the provisions in bidding document. |
|  |  | This cannot be taken up as most of the existing IED’s are on proprietary protocol. POWERGRID’s confirmation required on timeline for upgradation of non 61850 IED’s which need to be integrated with new SAS. |  |