| Sl. No. | # Volume/ Section | # Clause No. | # Description | # Bidder’s Query | # POWERGRID Reply |
| --- | --- | --- | --- | --- | --- |
| Volume-II (Technical Specifications) |  |  |  |  |  |
|  | III Bay Extension at 400/220kV Lucknow Sub-Station |  |  |  |  |
|  | 1.0) Section-Project_SS151 | 6. SUBSTATION AUTOMATION SYSTEM: | The Existing 400/220 kV Lucknow Substation is a conventional Substation (Control Panel) based where ALSTOM make SCADA - E-TERRA has been installed. At present data of all existing bays are reporting through ABB make RTUs (232 and 560), NTAMC Rack provided with GE make IED C264 and Extension Racks provided with GE make IED C264. Upgradation of Substation Automation System (based on IEC-61850) for complete Lucknow S/S is under present scope. Under the present scope of contract, the SAS system needs to be upgraded where all 400kV and 220kV Bays including present scope bays (Existing, under present scope and FUTURE as per SLD) and auxiliaries shall report. | As per section project, existing RTU to be replaced with new BCU’s. However, 1. Existing RTU panel totally Rusted and Retrofitting isn't feasible. 2. Cable Identification/ termination isn't practically possible. 3. If only Retrofitting is required then we need existing cable schedule, list of signals from PGCIL. Hence, we propose to supply & install new Panels with new BCU. With this solution, retrofitting/ replacement scope shall be complied. Kindly accept. | Additional BCUs under present scope required to upgrade the complete SAS as per TS may be installed in new/separate panel. Retro fitment of these additional BCU in existing panels is not envisaged. |
|  | 1.0) Section-Project_SS151 | 6. SUBSTATION AUTOMATION SYSTEM: | Necessary up-gradation of firmware of IED’s if required shall be deemed to be included elsewhere. Software for the configuration tool of IEDs shall be handed over by the vendor after execution of the contract | We wish to inform that, most of existing IED's are not 61850 compatibles (proprietary protocol) and same can't be integrated in New SAS. Hence - 1. We understand integration of IED's to proposed SAS applicable only for 61850 relays. Remaining relays will not be considered for SAS integration. Kindly accept. 2. Else, requesting PGCIL to change those proprietary protocol relays to IEC 61850 to integrate in to proposed SAS. | Integration of following IEDs in New SAS is envisaged as per TS. 1. Existing IEDs which are already IEC 61850 compliant. 2. Existing IEDs which are required to be upgraded to IEC 61850 compliant (by POWERGRID). 3. IEDs to be supplied under the present scope. |
|  | 1.0) Section-Project_SS151 | 6. SUBSTATION AUTOMATION SYSTEM: XIV | Existing SAS architecture, SLD drawing of the substation, List of Existing IEDs are enclosed as Annexure-VI, which shall be further engineered by the bidder.” | Below are the documents which isn't available in tender documents, 1. Existing SAS Architecture 2. Annexure-VI Kindly share. | - For Existing Architecture, kindly refer Amendment No-15. - For List of Existing IEDs, kindly refer Annexure-VII already attached with Section Project TS. |