| Sr. No | Clause No. | Clause Description | Bidder Queries | POWERGRID REPLY |
| --- | --- | --- | --- | --- |
|  | Point No. 7/Cl. 3.4 (B) Civil Works/Section Project & Point No. C/ Cl. 4 Specific Exclusions/Section Project | Soil Stabilization, Slope Protection Works & Retaining Walls shall be finalised in detail engineering stage | As per section projects 3.4 civil works point 7 -Soil Stabilization, Slope Protection Works & Retaining Walls shall be finalised in detail engineering stage, but as per Clause 4 (c) specific exclusion contouring and substation levelling is excluded. kindly confirm whether Soil stabilization, slope protection work & retaining wall is in present scope. If it is present scope kindly provide the tentative Qty of each item. | In present scope of works, Soil Stabilization, Slope Protection Works & Retaining Walls are not envisaged. However, , if these activities shall be required during detailed engineering, design and drawings shall be in the scope of bidder and same shall be measured under respective line items of BPS. |
|  | General | Soil Investigation Report | Please provide the soil investigation report of present scope nearby bore hole for our reference. | Soil investigation report shall be provided to the successful bidder during detailed engineering. |
|  | General | Drain | We Presume that Provision of drain in present scope area is not in bidder scope. kindly confirm. | Confirmed. Drains have not been envisaged in the present scope. However, if construction of drains shall be required during detailed engineering, same shall be dealt as per the contractual provisions. |
|  | CL.NO.3.E/ Section Project | The existing 400 kV Bus bar protection relay make & model is ABB make REB 500. Augmentation of existing Bus Bar protection for Bus Sectionaliser Bays is included in present scope. Peripheral Bay Units for present scope of bays may be used from dismantled peripheral units from other Section. The Bus Bar Protection for feeders of new Bus Sections of BUS I & II shall be done using new Distributed Bus Bar protection relays to be supplied under present scope. | As per section Project we understand that Dismantled Peripheral units of Section B (REB500) shall be used for new Bus sections of both Buses, whereas New Decentralised Busbar Protection shall be provided for Section B covering Bus sections. Kindly confirm our understanding. | New Distributed Bus Bar protection relays, along with Peripheral units of feeders including Bus Sectionaliser Bays( As per SLD)) of new Sections for both the 400KV Buses, is under present scope. The Dismantled Peripheral units for existing REB500 may be used against Bus Protection to include Bus Sectionaliser Bays only. |