| Sl. No. | Clause/ Drg. No. | Existing provision | Amended provision |
| --- | --- | --- | --- |
| 01 | Clause No. 9.1 of Section-Project, Rev. 00 | Clause No. 9.1 Bushing of 800kV, 420kV and 52kV voltage level shall be Oil filled condenser type with composite polymer insulator (housing) or RIP (Resin Impregnated paper) condenser type with composite polymer insulator (housing) or RIS (Resin Impregnated Synthetic) condenser type with composite polymer insulator (housing). | Deleted. Sl.No.1 of Amendment No-2. is superseded by this amendment |
| 02 | Clause No. 2.2.1 (I) of Section-Project, Rev. 00 New clause added. | 2.2.1 765/400/220kV Navsari (New) (South Gujarat) GIS SS: 7X500MVA, (765/√3)/(400/√3)/33kV Auto transformers (1-ph) under…………………….. ……………………………………………………. - (765/√3)/(400/√3)/33kV, 1-ph Autotransformers….. …………………. , insulating oil, etc. - ………………………………………………………….. …………………………………………………………. iv) (765/√3)/(400/√3)/33kV Autotransformer….. …………………………………………………. Further, LV side (33kV) of (765/√3)/(400/√3)/33kV Transformer shall have conventional AIS type termination. | 2.2.1 765/400/220kV Navsari (New) (South Gujarat) GIS SS: 7X500MVA, (765/√3)/(400/√3)/33kV Auto transformers (1-ph) under…………………….. ……………………………………………………. - (765/√3)/(400/√3)/33kV, 1-ph Autotransformers….. …………………. , insulating oil, etc. - ………………………………………………………….. …………………………………………………………. iv) (765/√3)/(400/√3)/33kV Autotransformer….. …………………………………………………. Further, LV side (33kV) of (765/√3)/(400/√3)/33kV Transformer shall have conventional AIS type termination. v) 800kV Bushing shall be suitable for GIS SF6/Oil Interface, as per IEC-62271-211. 420kV Bushing shall be suitable for GIS SF6/Oil Interface, as per IEC-62271-211. 52kV Bushing shall be RIP (Resin Impregnated paper) condenser type with composite polymer insulator (housing) or RIS (Resin Impregnated Synthetic) condenser type with composite polymer insulator (housing). |
| 03 | Clause No. 2.2.2 of Section-Project, Rev. 00 New clause added. | 2.2.2 765/400/220kV Padghe GIS SS: 3X500MVA, (765/√3)/(400/√3/33)kV Auto transformer (1-ph) under………………… ……………………………………….. - ………………………………… ………………………………… f. Mandatory spares (as per bid price schedule):……………………………………… testing at site. | 2.2.2 765/400/220kV Padghe GIS SS: 3X500MVA, (765/√3)/(400/√3/33)kV Auto transformer (1-ph) under………………… ……………………………………….. - ………………………………… ………………………………… f. Mandatory spares (as per bid price schedule):………… …………………testing at site. g. Bushing of 800kV, 420kV and 52kV voltage level shall be Oil filled condenser type with composite polymer insulator (housing) or RIP (Resin Impregnated paper) condenser type with composite polymer insulator (housing) or RIS (Resin Impregnated Synthetic) condenser type with composite polymer insulator (housing). |
| 04 | Clause No. 2.2.3 of Section-Project, Rev. 00 New clause added. | 2.2.3 765/400/220kV Banaskantha AIS SS: 3X500MVA, (765/√3)/(400/√3/33)kV Auto transformer (1-ph) under………………… ……………………………………….. - ………………………………… ………………………………… d. Mandatory spares (as per bid price schedule):……………………………………… testing at site. | 2.2.3 765/400/220kV Banaskantha AIS SS: 3X500MVA, (765/√3)/(400/√3/33)kV Auto transformer (1-ph) under………………… ……………………………………….. - ………………………………… ………………………………… d. Mandatory spares (as per bid price schedule):………………………………………………………… testing at site. e. Bushing of 800kV, 420kV and 52kV voltage level shall be Oil filled condenser type with composite polymer insulator (housing) or RIP (Resin Impregnated paper) condenser type with composite polymer insulator (housing) or RIS (Resin Impregnated Synthetic) condenser type with composite polymer insulator (housing). |
| 05 | Amendment No-II, Sl.No.3 | Clause No. 9.5: Clause No. 6.5.1 of Technical Specification, 765kV Auto-transformer, Rev. 08, is amended as below: Main conservator shall have air cell type constant oil pressure system to prevent oxidation and contamination of oil due to contact with moisture. Conservator Protection Relay (CPR)/Air cell puncture detection relay shall be installed to give alarm in the event of lowering of oil in the conservator due to puncture of air cell in service. Conservator shall be fitted with magnetic oil level gauge (Plug & socket type arrangement) with potential free high and low oil level alarm contacts and prismatic oil level gauge and Conservator Protection Relay. Plug & socket type arrangement with factory fitted cable of adequate length shall be supplied by OEM. Connection of plug and socket with cable at site is not acceptable. | Amendment No-II, Sl.No.3, Clause No-9.5 shall be read as Clause No-9.6 as below: Clause No. 9.6: Clause No. 6.5.1 of Technical Specification, 765kV Auto-transformer, Rev. 08, is amended as below: Main conservator shall have air cell type constant oil pressure system to prevent oxidation and contamination of oil due to contact with moisture. Conservator Protection Relay (CPR)/Air cell puncture detection relay shall be installed to give alarm in the event of lowering of oil in the conservator due to puncture of air cell in service. Conservator shall be fitted with magnetic oil level gauge (Plug & socket type arrangement) with potential free high and low oil level alarm contacts and prismatic oil level gauge and Conservator Protection Relay. Plug & socket type arrangement with factory fitted cable of adequate length shall be supplied by OEM. Connection of plug and socket with cable at site is not acceptable. |
| 06 | Annexure-H of Section-765kV Auto-transformer, Rev. 08 of Technical Specification | Annexure-H 1.1 KV GRADE POWER & CONTROL CABLES … … STANDARD TECHNICAL DATA SHEET (1.1kV GRADE XLPE POWER CABLES) … … STANDARD TECHNICAL DATA SHEET (1.1kV GRADE PVC POWER CABLES) … … STANDARD TECHNICAL DATA SHEET (1.1kV GRADE PVC CONTROL CABLES) … … | Annexure-H 1.1 KV GRADE POWER & CONTROL CABLES … … STANDARD TECHNICAL DATA SHEET (1.1kV GRADE XLPE POWER CABLES) – VOID (Parameters of Standard Technical Data Sheet shall not be referred to) STANDARD TECHNICAL DATA SHEET (1.1kV GRADE PVC POWER CABLES) – VOID (Parameters of Standard Technical Data Sheet shall not be referred to) STANDARD TECHNICAL DATA SHEET (1.1kV GRADE PVC CONTROL CABLES) – VOID (Parameters of Standard Technical Data Sheet shall not be referred to) |