| Sl. No. | Clause/ Drg. No. | Existing provision | Amended provision |
| --- | --- | --- | --- |
| 01 | Clause No. 9.1 of Section-Project, Rev. 00 | Clause No. 9.1 800kV, 420kV and 145kV Bushing shall be Oil filled condenser type with composite polymer insulator (housing) or RIP (Resin Impregnated paper) condenser type with composite polymer insulator (housing) or RIS (Resin Impregnated Synthetic) condenser type with composite polymer insulator (housing). | Clause No. 9.1 800kV Bushing shall be suitable for GIS SF6/Oil Interface, as per IEC-62271-211. 420kV Bushing shall be suitable for GIS SF6/Oil Interface, as per IEC-62271-211. 145kV Bushing shall be RIP (Resin Impregnated paper) condenser type with composite polymer insulator (housing) or RIS (Resin Impregnated Synthetic) condenser type with composite polymer insulator (housing). |
| 02 | BPS Schedule I & II 765kV Transformer Package: TR-35 New Item added | SI. No.; Item Description; Unit; Qty.. BOQ for 2x1500 MVA,765/400kV ICT,Navsari (New) SS: Mandatory Spares for 765kV Transformer. New Item. New Item. | SAP ID; Item Description; Unit; Qty. BOQ for 2x1500 MVA,765/400kV ICT,Navsari (New) SS: Mandatory Spares for 765kV Transformer. 1000060012; 420KV,2500A OIL TO SF6 BUSHING WITH METAL PARTS AND GASKETS; EA; 1. 1000060014; 800KV,2500A OIL TO SF6 BUSHING WITH METAL PARTS AND GASKETS; EA; 1. Corresponding to the above change existing “Price_schedule” stands replaced with “Price_schedule_Rev1” and is attached herewith. Note- Bidders are requested to consider the revised excel ‘Price_schedule_Rev1’ for bid preparation/submission. It may be noted that while submitting the bid, Bidders are required to change the excel file name from ‘Price_schedule_Rev1’ to ‘Price_schedule’. As per the provisions of the portal, it is mandatory to upload excel file with titled ‘Price_schedule’ (Bidders may refer user manuals at the portal https://etender.powergrid.in regarding submission of bid). |
| 03 | Clause No. 9.5 of Section-Project, Rev. 00 | New Clause added. | Clause No. 9.5: Clause No. 6.5.1 of Technical Specification, 765kV Auto-transformer, Rev. 08, is amended as below: Main conservator shall have air cell type constant oil pressure system to prevent oxidation and contamination of oil due to contact with moisture. Conservator Protection Relay (CPR)/Air cell puncture detection relay shall be installed to give alarm in the event of lowering of oil in the conservator due to puncture of air cell in service. Conservator shall be fitted with magnetic oil level gauge (Plug & socket type arrangement) with potential free high and low oil level alarm contacts and prismatic oil level gauge and Conservator Protection Relay. Plug & socket type arrangement with factory fitted cable of adequate length shall be supplied by OEM. Connection of plug and socket with cable at site is not acceptable. |