| Sl. no | Clause no w.r.t specification | Description as given in specification | Comments/ Clarifications | POWERGRID’s Reply |
| --- | --- | --- | --- | --- |
| 01 | Technical Specification, 765kV Autotransformer Rev. 08 | Bushing Type Test as per IS/IEC:60137 for all voltage class (Seismic test on 400kV and 800kV Bushings) | What is the actual meaning of Seismic test viz. Snap back test or Shaker table test or Just submission of calculations are sufficient for given Zone? Are these Seismic tests certificates required for Oil/SF6 Bushings? Is there any waiver possible for the seismic tests / Type tests? For Seismic test confirm requirement as per IEC 61463 (As IS standard is not followed by foreign manufacturers hence Seismic Zone III/IV/V does not indicate clear ground acceleration requirements). Refer below extract from IEC 61463 clause 6 & request confirmation on Ground acceleration to be referred by all manufacturers in order that all follow same procedure. | Technical specification is quite clear. Bidder shall quote as per provisions of bidding document. |
| 02 | Cl no. 2.2.1 (I) iv) of Section Project Page No – 5 of 11 | (765/√3)/(400/√3)/33kV Autotransformer shall be suitable for connecting both HV side (765kV) & IV side (400kV), with GIS SF6/Oil Interface, as per IEC-62271-211. Further, LV side (33kV) of (765/√3)/(400/√3)/33kV Transformer shall have conventional AIS type termination. | Request PGCIL to clarify type of bushing requirement are oil to SF6 or Oil to Air. | Please refer Clause No-1 of Amendment No-2. Technical specification is quite clear. |
| 03 | Cl no. 2.2.1 (II) of Section Project Page No – 5 of 11 | Mandatory spares | Mandatory spares are not mentioned in price schedule that means Spares are not required in this tender. Kindly confirm | Bidder to quote as per BPS. Also, please refer Clause No-2 of Amendment No-2. |
| 04 | Cl no. 8.0 of Section Project Page No – 10 of 11 | Exclusions : vi) Auxiliary power and control cables from Control Room/SPR to Transformer MB. However, Any special cable if required to be included from RTCC panel (under present scope), to employer’s C&R panel. | Request PGCIL to confirm that special cables requirement from CMB to C&R panel is not in supplier's scope. | The requirement of special cable required against RTCC panel, shall be finalized during detail engineering. |
| 05 | Cl no. 9.1 of Section Project Page No – 10 of 11 | Bushing of 800kV, 420kV and 52kV voltage level shall be Oil filled condenser type with composite polymer insulator (housing) or RIP (Resin Impregnated paper) condenser type with composite polymer insulator (housing) or RIS (Resin Impregnated Synthetic) condenser type with composite polymer insulator (housing). | Request PGCIL to clarify type of bushing requirement in this tender. | Please refer Clause No-1 of Amendment No-2. |
| 06 | Section-III / BDS / Sl. No. 30 / Completion Period | 1.; Seven (7) numbers of 500 MVA, (765/√3)/ (400/√3/33) kV Autotransformer (1-Ph) at 765/400/220kV Navsari (New) (South Gujrat) S/S; and Three (3) numbers of 500 MVA, (765/√3)/ (400/√3/33) kV Autotransformer (1-Ph) at 765/400/220kV Padghe GIS S/S; associated with Transmission Network Expansion in Gujarat to increase its ATC from ISTS part-B; 15 (Fifteen) Months. 2.; Three (3) numbers of 500 MVA, (765/√3)/ (400/√3/33) kV Autotransformer (1-Ph) at 765/400kV Banaskantha AIS S/S associated with Transmission Network Expansion in Gujarat to increase its ATC from ISTS part-C; 25 (Twenty Five) Months. Three (3) numbers of 500 MVA, (765/√3)/ (400/√3/33) kV Autotransformer (1-Ph) at 765/400/220kV Navsari (New) (South Gujrat) S/S associated with Transmission Network Expansion in Gujarat associated with integration of RE projects from Khavda potential RE Zone; 15 (Fifteen) Months. | 1. Considering the scope composition, we request you to kindly amend the completion period as follows for enabling us to participate in the bid. 1.; Seven (7) numbers of 500 MVA, (765/√3)/ (400/√3/33) kV Autotransformer (1-Ph) at 765/400/220kV Navsari (New) (South Gujrat) S/S; and Three (3) numbers of 500 MVA, (765/√3)/ (400/√3/33) kV Autotransformer (1-Ph) at 765/400/220kV Padghe GIS S/S; associated with Transmission Network Expansion in Gujarat to increase its ATC from ISTS part-B; 25 (Twenty Five) Months. 2.; Three (3) numbers of 500 MVA, (765/√3)/ (400/√3/33) kV Autotransformer (1-Ph) at 765/400kV Banaskantha AIS S/S associated with Transmission Network Expansion in Gujarat to increase its ATC from ISTS part-C; 25 (Twenty Five) Months. Three (3) numbers of 500 MVA, (765/√3)/ (400/√3/33) kV Autotransformer (1-Ph) at 765/400/220kV Navsari (New) (South Gujrat) S/S associated with Transmission Network Expansion in Gujarat associated with integration of RE projects from Khavda potential RE Zone; 25 (Twenty Five) Months. | Bidder to quote as per Biding documents. |
|  |  |  | 2. As per the tender requirement, 15 months completion period for 13 nos Transformer is very short. Due to shortage in CRGO availability, imported items supply affected due to Covid-19, this will impact delivery schedules of Transformers, Manufacturing lead time will be higher as compare to other smaller rating of Transformers. Hence request you to accept 18 months Completion period for this tender. | Bidder to quote as per Biding documents. |
| 07 | - | - | GA & SLD of Existing Sub-Stations [ i.e. 765/400/220KV GIS SS at Padghe & 765/400/220KV GIS SS at Banaskantha AIS SS] With reference to scope of works, we need to do the cabling works [SITC] between Digital RTCC to Transformer CMB. In this regard, we required GA of the existing Sub-stations. Request you to kindly provide the same for both sub-station [i.e. 765/400/220KV GIS SS at Padghe & 765/400/220KV GIS SS at Banaskantha AIS SS] | Requisite drawings shall be shared with successful bidder during detailed engineering. Bidder to quote as per BPS. Bidder is requested to visit site for better understanding of the layout. |