| Sl. No. | Ref Section | Provision in bidding document | Bidders Queries | POWERGRID Reply |
| --- | --- | --- | --- | --- |
| 1. | Vol. II TS Section project Cl. 2.4 | Design of substation and its associated electrical & mechanical auxiliaries systems includes preparation of single line diagram, electrical layout, foundation & cable trench layouts (including invert levels), …………………………………………………………………………………… other relevant drawings & documents required for engineering of all facilities within the fencing to be provided under this contract, are covered under the scope of the Contractor. | Kindly provide the tentative SLD, Plan & Section drawing of the switchyard. | As per bidding document, Preparation of SLD, Plan & section drawings of the switchyard is in the scope of the contractor. |
| 2. | Vol. II TS section project cl. 4.2 | Cl. 4.2 of Section Project Meteorological data Coastal Area consideration; No. | As per section project, Cl. No. 4.0, Physical and other parameter creepage distance is not indicated, however non-coastal area is indicated in respective clause. Considering same and as per Cl. No. 4.6 system parameters of GTR 25mm/KV creepage distance shall be considered for all equipment including LT Transformer bushings, please confirm. For Reactor bushing 31mm/kV Creepage shall be considered as per specification revision No. 11. Please confirm. | Provision of Bidding document is amply clear. Bidder to quote as per bidding document. Creepage distance for all equipment except 420kV Reactor and insulator for hardware strings shall be 25mm/kV. For 420kV Reactor bushing and insulator for Hardware strings creepage distance shall be 31mm/kV. |
| 3. | Vol. II TS section Project, Annexure II Specific requirement, Cl. 65 | Transmission line side insulator string along with hardware for line termination shall be in the scope of substation contractor. | Please provide conductor details to be considered for 220KV line side at substation end gantry. In absence of transmission line side conductor and conductor arrangement it is difficult to finalize the insulator and insulator hardware. We request PGCIL to include 220kV line side insulator and hardware in 220KV transmission line package considering approval related issues during DDE. Please confirm. | Bidder to quote as per bidding document requirement. Details of 220kV Line side conductor shall be intimated to successful bidder during detailed engineering. |
| 4. | Vol. II TS section Project, Annexure II Specific requirement, Cl. 75 | In case of new substation/switchyard, maximum spacing of Main Earthmat shall be considered as 30 M x 30 M, 24 M x 24 M, 16 M x 16 M & 12 M x 12 M for 765kV, 400kV, 220kV & 132kV switchyard respectively. Actual spacing for main earthmat shall be finalized during detailed engineering based on soil resistivity data and payment shall be made as per actual executed quantity at site. However, no cost compensation shall be considered in case of actual spacing of main earthmat finalized during detailed engineering is less than that mentioned above. For switchyard extensions, main earthmat spacing shall be considered same as that in the existing switchyard. | We request PGCIL to consider cost compensation based upon actual approved main earthmat layout during detail engineering. Please confirm. | Bidder to quote as per bidding document. |
| 5. | Vol. II TS section Power and control cable rev.06 | General | We understand ICT & Reactor MB unit will be looping to adjacent ICT/Reactor MB. Please confirm our understanding. | Refer Amendment no. 1 Sl. no.2. Cables for present package shall be paid as per unit rate. Power supply arrangement to ICT/Reactor shall be finalized during detailed engineering. |
| 6. | Vol. II TS section Power and control cable rev.06. Cl. 1.1.5 | Bidder may offer sizes other than the sizes specified in clause 1.1.4. In such case and for other application where sizes of cables have not been indicated in the specification, sizing of power cables shall be done keeping in view continuous current (including future bays/load requirement), voltage drop & short-circuit consideration of the system. | With reference to Cable specification, 9.0 Power & Control Cable Rev R6, we shall consider cable sizing calculation based on voltage drop & short-circuit consideration of the system for Re-sizing the power cables. Please accept & confirm. | Refer Amendment no.1, Sl. no.2. Cables for subject package shall be paid as per unit rate. Bidder to quote as per bidding document. |
| 7. | Vol.II TS section CRP rev.09 | General | Relay Setting calculation shall be provided by PGCIL, Kindly Confirm the same. | Confirmed. |
| 8. | General | General | 1. Please share Plot coordinates. 2. We presume that dismantling, if any at site is not in present scope of tender. | 1. Plot co-ordinate shall be provided to successful bidder during detailed engineering. 2. Dismantling of any existing structure at site is not envisaged under present scope. However, in case any such work comes at the time of detailed engineering the same shall be dealt with as per provisions of Contract. |
| 9. | General | General | We presume that Control Room Building shall be single storied. Please confirm. | Control room building may be one/two storied as per requirement that shall be decided during detailed engineering. |
| 10. | Vol. III BPS, Schedule III, Sl. no. 155, 174, 175, & 185 | 155; Misc. Structural steel including rails, embedments, edge protection angles, gratings etc. but excluding the reinforcement steel andsteel for lattice and pipe structures.; MT; 173. 174; FFPH Building - Civil Works All civil works as per drawing and specifications complete, including – brickwork, finishing (external and internal), windows etc. However, excavation, PCC,RCC and reinforcement shall be paid separately as per BPS; M2; 101. 175; All civil works as per drawing and specification but excluding excavation, PCC, RCC, reinforcement but including finishing (internal and external) etc & all civil works complete in all respect - Water Tank for Fire Fighting Pump House; EA; 1. 185; Control Room Building - Civil Works All civil works as per drawing and specifications complete, including - brickwork, finishing(external and internal), windows etc. However, excavation, PCC, RCC and reinforcement shall be paid separately as per BPS.; M2; 550. | We presume that structural steel to be used for item nos 174, 175, 185 i.e. FFPH, Water Tank & CRB will be paid under Sl. No. 155 for miscellaneous structural steel. Please confirm. | Item Nos. 174, 175 and 185 includes payment of structural steel as per TS. |
| 11. | Vol. III BPS, Schedule III, Sl. no. 196 & 197 | 196; 14.4.2 Providing, laying and fixing following dia RCC pipe NP2 class (light duty) in ground complete with RCC collars, jointing with cement mortar 1:2 (1 cement : 2 fine sand) including trenching (75 cm deep) and refilling etc as required. : 150 mm dia; M; 50. 197; 14.4.3 Providing, laying and fixing following dia RCC pipe NP2 class (light duty) in ground complete with RCC collars, jointing with cement mortar 1:2 (1 cement : 2 fine sand) including trenching (75 cm deep) and refilling etc as required. : 250 mm dia; M; 200. | We presume that 150 & 250mm dia NP2 class hume pipe required for connecting Tranformer local oil pit & common oil pit will be paid under Sl. No. 196 & 197. Please confirm. | Confirmed. |
| 12 | General | General | We presume that Equipment support structures may be Lattice or Pipe type. Bidder is free to choose the structure type between these. Please confirm. | Confirmed. |
| 13 | Vol III BPS Sch. 1, Sl. no. 39 | 39; Fabrication, galvanising and supply of 33kV Std Double Pole Structure including nuts, bolts, all type of washers, pack plates, step bolts and gusset plates excluding foundation bolts; EA; 1. | Double pole structure is mentioned in section project (CL. NO. 2.1.1.3 Civil works) for 11kV. Please include same in price schedule. | Double Pole structure specified in the BPS shall be suitable for 33kV equipment specified at clause no. 2.1.1.1f) of TS section-project. Bidder to quote as per BPS. As specified in Section – Projects development of design and drawing of the 33 kV Double Pole Structure is in scope of bidder. |
| 14 | General | General | Erection Hardware for 400kV Tie bay is not given for Chhatarpur Substation, while required. Kindly, confirm in which head we have to taken Erection hardware for Tie Bay. | Refer clause no. 5.0 schedule of quantities of TS section-project and also refer “typical module” drawing no. C/ENGG/STD/MODULE included with tender drawings. Accordingly, the erection hardware for Tie bay deemed to include in the Erection hardware items specified for main bays of the respective diameter in the BPS. |
| 15 | General | General | Land is identified/Acquired by PGCIL for Chhatarpur Substation or not. Kindly, Confirm. If, Yes, kindly share the coordinates of the same. | Presently proposed land details are not available with POWERGRID. Accordingly, the co-ordinates of the proposed land for substation shall be provided to successful bidder during detailed engineering. |
| 16 | Vol. II TS section Project, Annexure II Specific requirement, Cl. 65 | Transmission line side insulator string along with hardware for line termination shall be in the scope of substation contractor. | We presume that Line Side hardware fitting and insulators are not in the scope of bidder. Kindly, Confirm | As per the referred clause of TS, Transmission line side insulator string along with hardware for line termination shall be in the scope of substation contractor under present scope of work. |
| 17 | Vol. III TS section SAS Rev. 04 Cl. 4.1 | ……..Remote HMI (Remote HMI only if mentioned in section project)……..: | As per Technical Specfication, Remote HMI will be considered if specified in the section Project. But in Section Project Remote HMI is not mentioned. Kindly, confirm whether Remote HMI is in present scope or not. | Remote HMI is not envisaged under present scope. |
| 18 | General | General | We presume that we have supplied Steel Structure & Erection Hardware for present bays only. We have not consider Steel Structure & Erection Hardware for any Future Bay. Also, Bus extension for future bays is not in our scope. Kindly, confirm | Bidder to quote as per bidding document requirement. |
| 19 | Vol. II TS section Project Clause 2.1.1.1 w) | TS section Project Clause 2.1.1.1 w) Lattice and Pipe structures (galvanized): ……………………………………………………………… For diameter where 400/220kV ICT is to be terminated, the structure must also consider the load and deviation which is arising due to the interconnection with 220kV side. …………………………………………………………………………………………………………………………. | As per refered clause, please let us know the maximum deviation to consider in structure for diameter of 400/220kV ICT due to interconnection at 400kV & 220kV Side. | Angle of deviation shall be as per switchyard layout drawing to be developed by the contractor during detailed engineering. |
| 20 | Vol. II TS section Project Clause 2.1.1.1 w) Vol III BPS, Schedule I Sl. no. 38 | TS section Project Clause 2.1.1.1 w) Lattice and Pipe structures (galvanized): ……………………………………………………………… Erection Hardware for 400kV I type layout-Bus Work (For one diameter)as per technical specification; SET; 4. Bus work(s) may be optimized by the contractor by suitably considering the number of diameters in a bus work section…………………………………………………………………………………………………………………………. BPS, Schedule I Sl. no. 38 | We have noticed that as per clause 2.1.1.1 point no. w), Bus works shall be optimized consider the number of 400kV diameter. However as per BPS, Sr.no.38, Erection Hardwares for 400kV I type layout- Bus Work to be considered for one diameter. Kindly clarifty which clause has to be followed for Bus work. | The referred BPS item “Erection Hardware for 400kV I type layout-Bus Work (For one diameter) as per technical specification” is specified to quote diameter wise prices of erection hardware required for bus works by the bidders and 4 Nos. of 400kV diameters are envisaged for the proposed substation. Whereas the TS clause referred specifies that “Bus work(s) may be optimized by the contractor by suitably considering the number of diameters in a bus work section.” Bidder to quote as per bidding document requirement. |
| 21 | Vol. II TS section Project Clause 2.1.1.1 w) Vol III BPS, Schedule I Sl. no. 39 | TS section Project Clause 2.1.1.1 w) Lattice and Pipe structures (galvanized): ……………………………………………………………… Bus work(s) may be optimized by the contractor by suitably considering the number of diameters in a bus work section…………………………………………………………………………………………………………………………. BPS, Schedule I Sl. no. 39 Erection Hardware for 220kV layout (Double Main and Transfer Scheme)-Bus work (one Bay) as per technical specification; SET; 10. | We have noticed that as per clause 2.1.1.1 point no. w), Bus works shall be optimized for 220kV bays. However as per BPS, Sr.no.39, Erection Hardwares for 220kV layout- Bus Work to be considered for one bay. Kindly clarifty which clause has to be followed for Bus work. | The referred BPS item “Erection Hardware for 220kV layout (Double Main and Transfer Scheme)-Bus work (one Bay) as per technical specification” is specified to quote bay wise prices of erection hardware required for bus works by the bidders and 10 Nos. of 220kV bays are envisaged for the proposed substation. Whereas the TS clause referred specifies that “Bus work(s) may be optimized by the contractor by suitably considering the number of diameters (bays for 220kV layout) in a bus work section.” Bidder to quote as per bidding document requirement. |
| 22 | Vol. II TS section Project Clause 2.1.1.1 w) | Lattice and Pipe structures (galvanized): ……………………………………………………………… In case of 400kV switchyard, the Gantry structures including foundation bolts and fasteners are to be quoted per diameter wise. In each diameter, the bidder shall consider all required structures. The line take-off gantry structures shall be considered with ±30 degrees deviation and slack span of maximum 200m. …………………………………………………………….. The line take-off gantry structures shall be considered with ±30 degrees deviation and slack span of maximum 200m for 220kV. …………………………………………………………….. | As per refered clause, please provide the conductor tension to consider at take-off gantry for 400kV & 220kV lines. | Bidder to quote as per bidding document. Also, Kindly refer to Amendment no. 1 sl. no. 13. |
| 23 | Vol. II TS section Project Clause 2.1.1.1y) and and Vol. III BPS, Schedule 3, Sl. no. 212 | Telecommunication equipment & PMU (Qty as per BPS) 1) The broad Scope of the procurement of FO based Communication Equipment shall include planning, designing, engineering, supply, transportation, insurance, delivery at site, unloading handling, storage, installation, termination, testing, training and demonstration for acceptance, commissioning and documentation for following: i. SDH Equipment along with suitable interfaces and line cards. ii. All cabling, wiring, Digital Distribution frame patch facilities and interconnection to the supplied equipment at the defined interfaces, iii. System integration of all supplied subsystem iv. Integration with the existing communication system based on SDH and PDH of employer v. Integration of supplied subsystem with SCADA system, PLCC equipment, PABX of RLDC/SLDC, VOIP (SIP compliant) for voice. vi. Fibre Optic Approach Cable (FOAC) along with duct and Fibre Optic Distribution Panel (FODP) vii. Integration of new Communication equipment in the existing regional NMS. All required support to existing NMS vendor for integration of new Communication equipment. 2) The broad Scope of the procurement of PMU shall include planning, designing, engineering, supply, transportation, insurance, delivery at site, unloading handling, storage, installation, termination, testing and demonstration for acceptance, commissioning and documentation for PMU as per BPS and these PMU shall support IEEE C 37.118 protocols. These PMUs shall be integrated with Phasor data Concentrator (PDC) at RLDC/SLDC for the subject project. and 212; 170000501; Integration of PMU with the PDC (Phasor Data Concentrator) of RLDCs and respective SLDCs as required.; LOT; 1. | In BPS, we have not found separate line item for integration of PMU with Phasor data Concentrator (PDC) at RLDC/SLDC. Kindly clarify.include the same in BPS and also give the details of make & model of Phasor Data concentrator at RLDC/SLDC. PMU. Further, we are not envisaging any hardware upgradation/new supply/Software upgradation at PDC. Please confirm. | Line item for Integration of PMU with Phasor data Concentrator (PDC) at RLDC/SLDC is available at following location:- “In Sch – 3 at Sr. No. 212 of BPS for 400/220 kV Chhatarpur S/s .” All the configuration work required for integration of PDC (with NTAMC/RLDC/SLDC) at substation end, shall be in present scope of bidder. Thus, Bidder’s scope is limited up to substation end. |
| 24 | Vol. II TS section Project Clause 9.2 | In case of 220kV line protection panel, Numerical Distance protection relay as Main–I and Line Current differential relay (with back up distance protection feature) as Main- II shall be provided. Remote end relays for 220kV lines are not covered under present scope. | As per referred clause, Please let us the make & model of relay to consider the Line Current differential relay (with back up distance protection feature) as Main-II for 220kV lines. | Bidder may offer any make & model fulfilling requirement of bidding document. |
| 25 | Vol. II TS section Project Clause 2.1.1.3 Civil works, D) | Factor of safety for design of tower and equipment structures and foundations shall be as below: a) Factor of safety for design of tower, equipment structures shall be 1.5 under normal condition and 1.2 under short-circuit condition. b) Factor of safety for design of tower, equipment foundation shall be 1.5 in both normal and short circuit condition as per IS 456. c) Factor of safety for stability of tower, equipment foundation like overturning shall be 2 (without wind or seismic), 1.5 (with wind or seismic) for normal and short circuit condition as per IS 1904.” | We shall do the short circuit force calculations following the IEC - 865, Part-1, 1993 version. Please confirm | Confirmed. Also, Kindly refer to Amendment no. 1 Sl. no.13. |
| 26 | Vol. II TS Section Project Clause 2.1.1.1 u) | LED based Lighting and illumination for the switchyard area under present scope, for streets, Control Room cum administrative building, Switchyard Panel Rooms, Fire Fighting Pump house, DG Set area and LT station area, security room shall be provided by the contractor. | As per referred clause, We understand that illumination are to be provided peripheral road of substation. Kindly confirm our understanding is correct or not. | Please refer BPS, wherein Fixtures required for outdoor illumination are to be quoted as per unit rate for the specified indicative quantity. However, actual number & location of outdoor fixtures shall be finalized during detailed engineering. |
| 27 | General | General | Please let us know whether Control Room Building is Single/Double storey and also rooms to consider in Control Building. | Control room building may be single or double storey, which is to be decided during detail engineering. However approx. Area shall be as per BPS. |
| 28 | Vol. II TS Section Project Clause 2.1.1.1 n) | LT switchgear (AC/DC Distribution boards) considering present and future bays. AC/DC system shall be provided as per the specified present scope of work, including future provisions, and in line with the LT SLD enclosed at Annexure-I. Further, following shall also be noted: …………………………………….. | As per referred clause, We understand that the only space provisions (i.e. vacant modules) need to be provided for the feeders pertaining to future requirements in LT switchgears (MSB,AC/DCDB,MLDB,ELDB). Please confirm whether bidder's understanding is correct or not. | Complete Feeders for present and future bays defined in Clause no. 2.0 of TS section-project shall be provided in LT switchgears under present scope. |
| 29 | Vol.II TS section Project, Annexure II, Cl. no. 6 | The CSD shall be provided in Circuit breaker of switchable line reactor bay and in Main & Tie bay circuit breakers of Transformers (required for 765/400kV transformers only), line with non-switchable line reactors and Bus reactors. The CSD shall be supplied as per bid price schedules. | Based on scope of work specified in clause 2.0 scope of section project, We have noticed that the CSD for 420kV,3-ph Circuit Breaker shall be 08(eight) numbers instead of 02(two) Numbers for present scope of bays defined in section project( 03 number of transformer bay & 01(one) number of bus reactor along with associated ties bays). Kindly check and revise the quantity in BPS/clarify the same. | Bidder to quote as per bidding document requirement. CSD is not required for main and tie bays of 400/220 kV Transformers as clearly specified at referred clause of TS Section project: Annexure II specific requirement. Accordingly 2Nos. of CSD specified in BPS is correct. |
| 30 | Vol. II TS section Air Conditioning rev. 04 | General | Air- Conditioning heat load calculation shall be done on the basis of max/ min site temperature and unit will statisfactory work upto ambient temperature i.e. 50 deg C. Please confirm. | Quantity & Capacity rating of Air conditioning unit is already specified in referred clause of TS and BPS. Hence calculation of heat load is not applicable for subject package. However, each Air conditioning unit shall work satisfactorily up to ambient temperature i.e. 50 deg C. |
| 31 | Vol. II TS section battery and battery charger rev. 06 | General | To optimize the Battery sizing, battery room inside temperature shall be maintained between 20 - 24 deg C with Hot & Cold type AC units (working & standby) and battery design shall be done considering inside battery room temperature. Pls confirm. | Bidder shall quote as per bidding document requirement. Design temperatures are clearly specified in TS section battery and battery charger rev. 06 |
| 32 | General | General | Kindly provide the soil investigation report for 400/220kv Chhatarpur (New) substation. | Soil Investigation is in the scope of bidder. Bidder shall quote as per bidding document requirement |
| 33 | General | General | Kindly confirm us that how much depth of cutting/filling to be consider for land development. | Contouring and Site Levelling work is in scope of bidder. Depth of Cutting and filling shall be decided after finalization of FGL during detailed engineering. |
| 34 | Vol. II TS section GTR rev. 15, cl. 14.3 | 14.3 FACILITIES TO BE PROVIDED BY THE EMPLOYER 14.3.1 Employer shall make available the auxiliary supplies at a single point in the substation on chargeable basis. The prevailing energy rates of the state shall be applicable. All further distribution from the same for construction supply shall be made by the contractor. However, in case of failure of power due to any unavoidable circumstances, the contractor shall make his own necessary arrangements like diesel generator sets etc. at his own cost so that progress of work is not affected and Employer shall in no case be responsible for any delay in works because of non-availability of power. 14.3.2 Employer shall make available construction water supply at a single point in the substation. All further distribution for the same shall be made by the Contractor. In case of non-availability or inadequate availability of water for construction work, the contractor shall make his own arrangement at his own cost and the Employer shall in no case be responsible for any delay in works because of non-availability or inadequate availability of water. | Kindly confirm availability of the sources for 415V constructional power and water near the proposed site. | Kindly refer to cl. 14.3 of TS section GTR rev.15 which is amply clear. |
| 35 | General | General | We presume that space shall be provided at site for storage & site office construction at free of cost. Please confirm. | The space for storage and site office shall be provided to the contractor subject to availability at site. However, the overall responsibility of construction of site office and storage shall lie with the contractor in accordance with the provisions of the bidding documents. |
| 36 | Vol.II TS Section Upto 400kV Shunt Reactor Rev. 11, Cl. No. 7.5.1 | Conservator shall be fitted with magnetic oil level gauge with potential free high and low oil level alarm contacts and prismatic oil level gauge and Conservator Protection Relay | Please clarify the type of MOG to be supplied for this project (Whether the requirement is Plug and Socket type or not). | Plug and socket type MOG supply is not mandatory, however Bidder may also can supply plug and socket type MOG. |
| 37 | Vol.II TS Section Upto 400kV Shunt Reactor Rev. 11, Cl. No. 22.1.xxiv | Fibre optic sensor based temperature measuring system (applicable for 400kV Reactor) | Specification of Fibre optic sensor-based temperature measuring is not mentioned in POWERGRID Technical Specification. Moreover, it is not called in BPS. Therefore, we understand that FOTS system is not applicable. Kindly confirm. | Confirmed |
| 38 | Vol. II TS Section Project, Annexure II, Specific requirement rev.06, Cl. no. 75 | In case of new substation/switchyard, maximum spacing of Main Earthmat shall be considered as 30 M x 30 M, 24 M x 24 M, 16 M x 16 M & 12 M x 12 M for 765kV, 400kV, 220kV & 132kV switchyard respectively. | We understand that there shall be same grid spacing for all voltage level in case of substation having multiple volatge level. Please confirm. Also in this regard, as Chhatarpur substation is 400/220kV, therefore kindly confirm whether maximum grid spacing shall be 24m(of 400kV) or 16m(of 220kV). | Maximum spacing for 400kV switchyard shall be 24m and 220kV switchyard area shall be 16m |
| 39 | Vol. II TS Section Project, Cl. 2.1.1.1 w) | Lattice and Pipe structures (galvanized): Towers, Beams and all Equipment support structures except support structure for circuit breaker. | We understand that lattice structure for equipment support is also acceptable. Please confirm. | Confirmed |
| 40 | Vol. II TS Section Project, Cl. 2.1.1.1 w) | In the bid price schedule, the structures including foundation bolts and fasteners are indicated in the form of sets. In case of 400kV switchyard, the Gantry structures including foundation bolts and fasteners are to be quoted per diameter wise. In each diameter, the bidder shall consider all required structures. The line take-off gantry structures shall be considered with ±30 degrees deviation and slack span of maximum 200m | We understand that 3 gantry arrangement is also acceptable. Please confirm. | Confirmed. Refer Amendment no. 1, sl. No. 13 and Annexure VI of TS section project (attached along with amendment no.1) wherein it is specified that for new 400 kV AIS switchyard with one & a half breaker switching scheme, three gantry type arrangement (i.e. arrangement having single gantry in Tie bay) shall be considered. |
| 41 | Vol. II TS Section Project, Cl. 2.1.1.1 s) | Erection Hardware: This item of BPS includes Insulator strings and hardware, Disc Insulators/Long Rod Insulators (as applicable), conductor(s), Al tube, bus-bar materials, cable trays & covers, Bay MB, spacers, clamps & connectors (including terminal……................... | We request POWERGRID to quantify the insulator string and hardware as unit rate items in line with practice seen in some of the other recent tenders of PGCIL | Refer Amendment no. 1, sl. No. 5, 6, 7, 8 and 12 for inclusion of separate items for String hardware along with insulators in BPS. |