| Sl.no | Tender Reference | Clause/Page number | Description | Query | Employer's Reply |
| --- | --- | --- | --- | --- | --- |
| 1 | - | General | ALMM requirement | Please confirm whether modules in the project should be under ALMM list. | Kindly refer to Note-4 of clause no. 3.6 of Chapter: A-1 SOLAR PHOTOVOLTAIC (SPV) MODULES of Technical Specification, Part-B (Chapter-A: DC System) regarding approved Models and Manufacturers as per MNRE guidelines/orders. |
| 2 | Technical Specification | P a r t - A : Section-Project (Subsection-2) /Page 5 | The Bidder shall terminate the HT cable from 33 kV HT switchgear to Power transformer located at 220 kV/33 kV substation to be built by Employer as per tender SLD. All hardware required for termination of 33kV cable at 33/220kV Power Transformer end shall be in bidder’s scope. | We understand that ROW for laying of cable shall be the responsibility of Employer.Pls confirm. | Kindly refer to the drawing titles "General Arrangement-Nagda Solar Power Plant" attached with Technical Specifications, wherein tentative location of 220/33kV substation (within the Plot boundary) is indicated. Further, in line with clause no. 12.0 of Chapter:1-A of Technical Specification, Part-A : Section-Project (Subsection-1), ROW clearance is under Bidder's scope. |
| 3 | Technical Specification | P a r t - A : Section-Project (Subsection-2) /Page 26 | PROVENESS CRITERIA | We understand that the said criteria shall be applicable in execution stage | Confirmed. |
| 4 | Technical Specification | P a r t - A : Section-Project (Subsection-2) /Page17 | *Starts from date of commissioning of full capacity | Pls define "Commissioning" as the same is also linked with payment terms | In line with clause no. 1.0 of Chapter: D-4 PROJECT COMMISSIONING AND OTHER GENERAL REQUIREMENTS of Technical Specification, Part-B (Chapter-D: General Systems), after successful completion of trial run and acceptance by Employer, SPV Plant shall be deemed to be successfully erected & fully commissioned subject to acceptance/approval by SLDC/DISCOM/MPPTCL. |

| Sr. | Chapter No. | Clause No. | Page No. | Tender Term | Bidders's Query | Employer's Reply/ Clarification |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | 3 | 3.6 | 21/139 | The Switchgear shall have an internal Arc Classification of IAC FLR corresponding to system fault current. | Bidder would like to propose only Indoor panel as IAC type as type test is available with OEM. Outdoor panels shall be without IAC as IAC type test is not available with OEMs due to manufacturing constraints of meeting IP55 while providing chimney for pressure release in case of internal arc. | Bidder shall quote as per provisions of bidding documents. |
| 2 | B3.A | 1_xviii | 46 | Bidder shall furnish over fluxing char. up to 150% | As per tender 140% for 5sec is required which we are complying however for 150% we would suggest a time lmimt of max. 1sec. | Bidder shall quote as per provisions of bidding documents. |
| 3 | IDT | 2.1.1 | 51 | HV Cable boxes shall be of phase segregated air insulated type & shall be of sufficient size to accommodate Employer’s cable & termination. Phase segregation shall be achieved by insulating barriers (for 3.3 kV and above side) | Bidder would like to propose non sagregated cable box as a standard type tested product. | Bidder shall quote as per provisions of bidding documents. |
| 4 | Aux. transformer | 2.11 | 63 | HV Cable boxes shall be of phase segregated air insulated type | Bidder would like to propose non sagregated cable box as a standard type tested product. | Bidder shall quote as per provisions of bidding documents. |
| 5 | ChapterB_B4_AC System_AC Cables |  |  | All cables shall be flame retardant, low smoke (FRLS) | Bidder would like to propose Non FR type cables for all types of power cables laid in PV field (DC & AC) and FRLS type for all LV & Control cables laid at Inverter stations or MCR. | Bidder shall quote as per provisions of bidding documents. |
| 6 | HT Power cable | 4 | 69 | The standard length for HT power cables shall be 1000 meter for all single core cables and 750 meters for 3 core cables | Standard drum length of 500mm available with vendors for 33kV cables hence same is being proposed by bidder. | Bidder shall quote as per provisions of bidding documents. |
| 7 | ChapterB_B5_Cable installation method | 2 | 75 | For derating, the ambient temperature for directly buried cables shall be taken as 40° C and 50° C for cables laid in air. | Bidder would like to propose 30 Deg cel ambient ground temperature for derating and 40Deg Cel for air. 50Deg Cel shall be considered in case ambient air temperature is more than 40 Deg. Cel. | Bidder shall quote as per provisions of bidding documents. |
| 8 | Trenches | 2 | 75 | PCC flooring of built-up trenches shall be sloped for effective drainage with sump pits and sump pumps. | PCC floored trenches shall be provided only in MCR. Trenches in PV field shall be excavated earthen trench. | Bidder shall quote as per provisions of bidding documents. |
| 9 | B8_Earthing System | 3 | 109 | The Contractor shall furnish the detailed design and calculations as per IEEE 80/IS 3043 for Employer's approval for equipment earthing | IS 3043 shall be followed for earthing design of PV array, inverter Station & MCR. IEEE80 shall be followed for Switchyard which is not a part of this package. | Bidder can use IS 3043 for earthing design of PV array, inverter Station & MCR. |
| 10 |  | 9 | Average Illumination level | Average 10 lux for periphery lighting | Average 5 lux between two light poles shall be sufficient. | Bidder shall quote as per provisions of bidding documents. |
| 11 | 220kV Line |  |  | Existing TL (220kV, 33kV, 11kV, LT) line inside proposed boundary. | Kindly confirm the shifting of existing TLs to be in Developer's (PGCIL) Scope before NTP. | Diversion of existing 220kV Transmission line, 33kV HT line and LT lines away from the plot is under Employer's scope. |
| 12 | Plant Area |  |  |  | 280Acres considered excluding Switchyard. Kindly confirm if additional land parcel can be provided to meet the generation obligations. | Approx. 280 Acres of land is including the area of 220/33kV substation as indicated in "General Arrangement" drawing attached with Technical Specifications. |
| 13 | TS-Part-A-Section-Project-SS1 | F | 14 | Design Wind Pressure, min, Pd (N/m2)- 890 N/m2 | Kindly allow Design wind pressure as per actual site condition and IS 875 PART-3 | Bidder shall quote as per provisions of bidding documents. |
| 14 | TS-Part-A-Section-Project-SS1 | A | 7 | Storeroom (Pre-Engineered Building)-1 no | Kindly allow to use ready made porta cabin (container) | Bidder shall quote as per provisions of bidding documents. |
| 15 | TS-Part-B-Chapter-D-General Systems | Part B-D-3,1.1 | 12 | Bidder shall provide permanent arrangement for module washing in the SPV Plant. This shall include installing storage tank/deep tube/bore wells with pump and motor, requisite storage arrangement and laying network of HDPE pipe conforming to IS 4984 | Kindly allow to use UPVC piping network. Piping shall be laid 300 mm below ground | Bidder shall quote as per provisions of bidding documents. |
| 16 | TS-Part-B-Chapter-D-General Systems | Part B-D-3,1.1 | 12 | The opening pipes for fixing the movable/Hose pipes for spraying water on module shall be made of GI pipe | Kindly allow to use UPVC Pipe | Bidder shall quote as per provisions of bidding documents. |
| 17 | TS-Part-B-Chapter-D-General Systems | Part B-D-3,1.5 | 12 | Maximum length of hose pipe shall be 50 meters from tapping point | Kindly allow to use up to 80 meter length hose pipe | Bidder shall quote as per provisions of bidding documents. |
| 18 | TS-Part-B-Chapter-D-General Systems | Part B-D-3,1.6 | 12 | The entire water washing system shall be tested for minimum 0.5 N/mm2 or double the maximum working pressure, whichever is greater. | Kindly allow 0.3 N/mm2 working pressure | Bidder shall quote as per provisions of bidding documents. |
| 19 | TS-Part-B-Chapter-C-Civil works | Part-B, C-3, 1.1 C) | 9 | The size of the foundation shall be decided based on the site conditions and geotechnical investigation report however the minimum diameter of the foundation shall not be less than 300 mm and depth less than 1000mm. | Kindly allow min depth to be as per design or soil report. | Bidder shall quote as per provisions of bidding documents. |
| 20 | TS-Part-B-Chapter-C-Civil works | Part-B, C-4, 6.0 A | 15 | the surface shall be prepared by Manual Cleaning and provided with Primer Coat of Chlorinated Rubber based Zinc Phosphate Primer of Minimum 50 Micron Dry Film Thickness (DFT). | For the portion of Steel surfaces embedded in Concrete, for column Hot dip galvanization with Avg. 80 micron Coating. Other than HDG Material for reinforcement and general foundation we proposed 500 CRS | As already indicated at Clause no. 6.0 of C-4 of Technical Specification, Part-B (Chapter-C: Civil Works), the referred para is applicable for coastal areas. Bidder shall quote as per provisions of bidding documents. |
| 21 | TS-Part-B-Chapter-C-Civil works |  |  |  | MMS material specification has been provided in table-A & B however we have summarised both as mentioned below: 1.Column- HDG. Avg 80 micron. With 2.0 min thick, Grade E-250 mpa 2.Rafter- Galvalume AZ 150, With 1.2 min thick, Grade E-550 mpa 3.Bracings- Galvalume AZ 150, With 1.2 min thick, Grade E-550 mpa 3.Purlin- Galvalume AZ 150, With 0.9 min thick, Grade E-550 mpa 4.Connecting Members/Cleat- HDG. Avg 80 micron. With 2.0 min thick, Grade E-250 mpa Kindly confirm the above mentioned materials | Bidder shall quote as per provisions of bidding documents. |
| 22 | TS-Part-B-Chapter-C-Civil works | Part-B, C-5, 2.0 B | 18 | Inverter Rooms:Pre-Engineered Building in line with PEB Tender drawing & technical specification (IR PEB shall be provided only in non-coastal area), | We are proposed to use outdoor inverter foundation with open canopy, Kindly confirm | Kindly refer Amendment-1. |
| 23 | TS-Part-B-Chapter-C-Civil works | Part-B, C-5, 2.0 B | 24 | SPECIFICATION OF STOREROOM: The height of store shall be minimum 5 meters and it shall be covered from all four sides. The store PEB size shall be minimum 200 square meter (width of approx. 7-10m) | we recomened size of store room of 10 meter x 5 meter x 3.5 meter height, please confirm | Bidder shall quote as per provisions of bidding documents. |
| 24 | TS-Part-B-Chapter-C-Civil works | Part-B, C-5, 4.0 B | 28 | The oil pit shall be filled with stones of 40 mm size uniformly graded. | Only 1/3 of total quantity filled by 40 mm size stone as per IS 10028 | Bidder shall quote as per provisions of bidding documents. |
| 25 | TS-Part-B-Chapter-C-Civil works | Part-B, C-5, 6.0 B | 29 | The drains shall be trapezoidal or rectangle section made of hard surface lining (stone masonry/pitched, Boulder, Precast cement concrete/stone slab, in-situ cement lime/concrete lining, soil cement lining, etc.) | Kindly allow earthen drain (unlined) also as per site condition | Bidder shall quote as per provisions of bidding documents. |
| 26 | TS-Part-B-Chapter-C-Civil works | Part-B, C-5, 6.0 f | 30 | Provision of culverts and their design to be submitted separately. The road on the culvert portions of the drains shall be concrete road. | Kindly allow without concrete road above the culvet, we are provide sufficient distance between pipe culvert and road. | Bidder shall quote as per provisions of bidding documents. |
| 27 | TS-Part-B-Chapter-C-Civil works | Part-B, C-5, 8.1 | 31 | Approach Road: The approach road to the Solar Power Plant shall originate from the main approach road and connect to all Inverter rooms, CMCS building, module cleaning station and gates. Approach road shall be 3.0-meter-wide with 500 mm wide shoulder on both sides. Moorum/brick, with a minimum 100 mm thick shall be provided for the shoulder along the approach road. The crown of the road shall be minimum 150 mm above FGL. The final finished roads shall have a camber of 1in50. | 1. Approach road- Main public road to main gate- Topping shoude be premix carpet 20 mm thick., 3.5 meter wide road with both side 500 mm shoulder. Kindly confirm | Bidder shall quote as per provisions of bidding documents. |
| 28 | TS-Part-B-Chapter-C-Civil works |  | 31 |  | 2. Access road- Main gate to CMCS - Topping shoude be granular with soil mix 20 mm thick., 3.5 meter wide road with both side 500 mm shoulder. Kindly confirm | Bidder shall quote as per provisions of bidding documents. |
| 29 | TS-Part-B-Chapter-C-Civil works |  | 31 |  | 3. Internal road- CMCS to inverter room - Topping shoude be granular with soil mix 20 mm thick., 3.0 meter wide road with both side 500 mm shoulder. Kindly confirm | Bidder shall quote as per provisions of bidding documents. |
| 30 | TS-Part-B-Chapter-C-Civil works |  | 31 |  | 4. Pheripheral road - Topping shoude be granular with soil mix 20 mm thick., 3.0 meter wide road with both side 500 mm shoulder. Kindly confirm | Bidder shall quote as per provisions of bidding documents. |

| Sl. No | Section | Page No. | Clause No./ Drg.No. | Description as per Tender Specification | Query | Employer's Reply/ Clarification |
| --- | --- | --- | --- | --- | --- | --- |
| 1 |  |  | General | Cohesion & internal friction angle is not available in soil investigation report | Kindly furnish the same if it is available | Soil investigation data furnished with the bid document is only for refrence purpose. Detail geotechnical investigation is included under Contractor's scope of works. |
| 2 |  |  | General | Premix carpet was mentioned in the tender drg. | Is it optional or mandatory.kindly confirm | In line with clause no. 8.1 of C-5 CIVIL & STRUCTURE WORKS – GENERAL DESIGN CRITERIA of Technical Specification, Part-B (Chapter-C: Civil Works) and drawing for "Typical Details of Road" attached with Technical Specifications, 20 mm thick premix carpet shall be provided. |
| 3 |  |  | General | Only approach road is mentioned in tender drg. | It is understood that peripherial road is not mandatory.kindly confirm | Road layout shall be finalized during detailed engineering meeting the requirements of Technical Specifications. |
| 4 |  |  | General |  | Kindly furnish Vicinity map and site KML file | GPS coordinates of the proposed site and General Arrangement drawing indicating the approximate boundary of plot has already been provided in Technical Specifications. Further, “.kmz” file indicating the approximate complete plot area, including area for establishment for 220/33kV substation, is attached with Amendment-1 for reference purpose only. |
| 5 |  |  | General |  | Shall the bidder allow to use outdoor container solution for compact sub station instead of PEB IR? | Kindly refer Amendment-I. |
| 6 |  |  | General |  | Water supply for module washing system scope to be clarified. | Kindly refer to clause no. 1.0 of D-3 MODULE CLEANING SYSTEM of Technical Specification, Part-B (Chapter-D: General Systems) for details of module washing system. |
| 7 |  |  | General |  | What will be the size of stores room since tender drg is not available. | Kindly refer clause no. 2.3 of C-5 CIVIL & STRUCTURE WORKS – GENERAL DESIGN CROTERIA of Technical Specification, Part-B (Chapter-C: Civil Works) for details of store room. |
| 8 |  |  | General |  | Kindly allow for PEB control room to expedite the work. | In line with clause no. 2.0 of CHAPTER: 3-A TERMINAL POINT AND EXCLUSIONS of Technical Specification, Part-A : Section-Project (Subsection-3), Construction of CMCS building is excluded from the scope of works of subject package. Further, Space shall be provided in Switchyard Control Room (envisaged under separate package) for accommodating the Solar SCADA and other equipment. |
| 9 |  |  | General | Typical cross section of approach road. | Kindly allow to derive the sectional thickness based upon site CBR value. | Bidder shall quote as per provisions of bidding documents. |
| 10 |  |  | General |  | Tentative civil FQP frequency is very stringent for short term project. FQP to be frequency & class of check to be reviewed while executing the work. | Kindly refer clause no. 3.0 of E-2 of Technical Specification, Part-B (Chapter-E: Quality Assurance) for Field Quality Plans (FQP). |
| 11 |  |  |  | Approximately 280 acres of land in a single parcel | For minimum DC Capacity of 118MWp with alloted area of 280Acre means 2.37Acre/MWp is very compact to plot the array, May please provide few more acre of land. | Bidder shall quote as per provisions of bidding documents. |
| 12 |  |  |  | Electrical drawing | Bidder understanding is both outgoer feeder to power tranasformer may or may not be of same rating- Please confirm | In line with clause no. 7.0 of CHAPTER: 1-A PROJECT INFORMATION of Technical Specification, Part-A: Section-Project (Subsection-1), the outgoing feeders from 33kV HT Switchgear shall be connected to LV side of 2x50 MVA220/33kV Transformers located in 220/33kV substation (The Transformers are being provided under separate package). |
| 13 | Indicative vendor list / Subsys-tem- C&I | 28 | 10 | PLC Based SCADA System | Bidder’s in-house manufactured DCS which is field proven in power plants gives the Customer following advantages: (i) Better immunity to noise. (ii) Scalable and Flexible system (iii) Comprehensive Diagnostics (iv) Centralized alarms, events and historian (v) Faster inter communication (vi) Unified Information Management, (vii)Common engineering platform & Unified diagnostics, (viii) Single family hardware solution, (ix) Better response time. (x) Single window for future expansion. (xi) Better Spares Management & Inventory reduction. etc. (xii) Supports renovation and modernization. Hence Customer is requested to accept BHEL EDN inhouse man-ufactured DCS based controls for SCADA System. Kindly Confirm. | Bidder shall quote as per provisions of bidding documents. |
| 44 | TS cover-SS1 | 7 | 7 | Bidder’s present scope shall include termination of HT cable from HT switchgear to the LV Side of the 220kV/33 kV power transformer at the substation to be built by Employer. | Please inform the distance between the plant boundary and 220/33kV substation | Kindly refer to the drawing titles "General Arrangement-Nagda Solar Power Plant" attached with Technical Specifications, wherein tentative location of 220/33kV substation (within the Plot boundary) is indicated. |
| 45 | TS cover-SS1 | 7 | 6 | CERC (Grant of Connectivity, Long Term Access and Medium-term Access in Interstate Transmission and related matters) Regulation 2009 | We understand that connectivity application and LTA and medium terms access will be under employer scope. Please inform | Connectivity application and LTA/Medium term access are under Employer's scope. However, in line with clause no. 7.0 of Chapter: 1-A and clause no. 2.0.(16) of Chapter: 1-B of Technical Specification, Part-A : Section-Project (Subsection-1), the contractor shall facilitate for the connectivity application by Employer for solar plant. |
| 46 | TS cover-SS1 | 7 | 6 | CERC’s revised procedure for “Grant of Connectivity to Projects based on renewable sources to inter-state transmission system” | We understand that connectivity application and LTA and medium terms access will be under employer scope. Please inform | Kindly refer to our reply at sl. no. 45 above. |
| 47 | TS cover-SS1 | 9 | 12 | ROW Clearance- to be arranged by bidder | Please inform if there are any right of Way issues. We request that any right of way to be in the scope of PESL | Bidder shall quote as per provisions of bidding documents. |
| 48 | TS cover-SS1 | 9 | 12 | Approval for water required for Project from concerned authority | We kindly request that these clearance and approvals to be taken by PESL. Please consider | Bidder shall quote as per provisions of bidding documents. |
| 49 | TS cover-SS1 | 9 | 12 | Any other Approval, permit/clearance from State Govt & local body | We kindly request that these clearance and approvals to be taken by PESL. Please consider | Bidder shall quote as per provisions of bidding documents. |
| 50 | TS cover-SS1 | 9 | 12 | MOEF Clearance (if, applicable) | We kindly request that these clearance and approvals to be taken by PESL. Please consider | Bidder shall quote as per provisions of bidding documents. |
| 51 | TS cover-SS1 | 19 | Appendix-4-1 | Liquidated damages per unit (kWh) shortfall in generation during PG Test = INR 38.97 (N) N is NPV of value R for 25 years considering the discount factor | 38.97 is on very higher side. We kindly request to reduce the value to 30. | Bidder shall quote as per provisions of bidding documents. |
| 52 | TS cover-SS1 | 19 | Appendix-4-2 | Maximum liquidated damages on account of failing to meet guaranteed generation during PG test for the solar PV project shall be limited to 15% of the contract value (excluding O&M charges). | We kindly request that maximum LD on shortfall in PG test to be limited to 5% of the contract price | Bidder shall quote as per provisions of bidding documents. |
| 53 | TS cover-SS1 | 21 | Chapter 1B-1.ii | Topo-Survey and Contour map | We kindly request autocad drawings to be submitted for Topo-survey and contour map | Kindly refer Amendment-1 |
| 54 | TS cover-SS1 | 23 | 2.ii | Topography survey (if required) and Geo-technical investigation of complete plot area including area for 220kV substation | 220kV substation is in scope of PESL hence Geo-tech and Topo for 220kv is to be conducted by PESL | As already mentioned at clause no. 2.0 (2) of Chapter: 1-B of Technical Specification, Part-A : Section-Project (Subsection-1), Employer has already carried out the contour survey of the site and a copy of contour layout is attached with Tender drawings. Further, in line with above clause, the detailed Topography survey (if required) and Geo-technical investigation of complete plot area including area for 220kV substation is included under Contractor's scope of works. Also, refer Amendment-1. |
| 55 | TS cover-SS1 | 23 | 2.iii | Cutting & Up-rooting of tress (if required) | We kindly request cutting and up-rooting of trees and disposal to be in the scope of PESL | Bidder shall quote as per provisions of bidding documents. |
| 56 | TS part-B chapter-D | 19 | 4a | Employer shall take Fire & Allied Peril insurance during O&M period. Insurance for theft to be taken by contractor. | Please inform in case of damage to equipment which is covered under Fire & Allied peril policy then PESL will reimburse the actual cost of equipment replaced or the amount paid by the insurance agency | Kindly refer Amendment-I. |
| 57 | TS part-B chapter-D | 22 | 5 | Following factors shall be considered for computing the “target Generation” and shortfall | Please inform the quoted energy generation will be changed w.r.t actual radiation at site. Please confirm | Quoted energy shall remain same. Target generation shall be modified as per relevant clauses in the Technical Specification. |
| 61 | General |  |  | Infrastructure of SPPD/SPIA | Please inform What is the date of availability of infrastructure of Solar Park Implementing agency – Road, Drain, power evacuation and communication network | Bidder shall quote as per provisions of bidding documents. |
| 64 |  |  |  | Factors considered for Validation of guaranteed generation | Please confirm that the actual values of radiation, temperature when compared to reference data, grid loss hours, module degradation and grid limitation hours,if any shall be considered in the validation of annual guaranteed generation. | Bidder shall quote as per provisions of bidding documents. |