## MB-Civil
POWER GRID CORPORATION OF INDIA LTD.
Details of Measurement
Name Of Work : : Fabrication of 2-Nos Closed Store shed for Oil shed Drum/ hardware fittings at Bhadla-2 Substation
Schedule Items-CIVIL
Sr.No | DSR-2023 Item No | Dsecription of works | Nos. |  | Length (M) | Breadth (M) | Height/Depth (M) | Quantity | Unit
1 | 2.28 | Surface dressing of the ground including removing vegetation and inequalities not exceeding 15 cm deep and disposal of rubbish, lead up to 50 m and lift up to 1.5 m. All kinds of soil
|  | Surface Area | 2 |  | 16.5 | 16.5 |  | 544.5 | sqm
2 | 2.8.1 | Earth work in excavation by mechanical means (Hydraulic excavator) / manual means in foundation trenches or drains (not exceeding 1.5 m in width or 10 sqm on plan), including dressing of sides and ramming of bottoms, lift upto 1.5 m, including getting out the excavated soil and disposal of surplus excavated soil as directed, within a lead of 50 m 2.8.1 All kinds of soil.
|  | Footing (1500x1500) | 2 | 12 | 1.95 | 1.95 | 1.2 | 109.512 | cum
3 | 2.25 | Filling available excavated earth (excluding rock) in trenches, plinth, sides of foundations etc. in layers not exceeding 20cm in depth, consolidating each deposited layer by ramming and watering, lead up to 50 m and lift upto 1.5 m.
|  | IN footing-Excavated Earth | [5 empty] | 109.512
|  | Deduction-Footing Qty(RCC) | [5 empty] | -16.2
|  | Deduction-Column Qty(RCC) | [5 empty] | -5.832
[6 empty] | Total Qty |  | 87.48 | cum
4 | 4.1.8 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering - All work up to plinth level : 1:4:8 (1 Cement : 4 coarse sand (zone-III) derived from natural sources : 8 graded stone aggregate 40 mm nominal size derived from natural sources)
|  | Footing (1500x1500) | 2 | 12 | 1.65 | 1.65 | 0.075 | 4.9005 | cum
|  | Flooring | 2 |  | 16.5 | 11.5 | 0.15 | 56.925
|  | Ramp Area | 2 | 1 | 2 | 2 | 0.15 | 1.2
[6 empty] | Total Qty |  | 63.0255 | cum
5 | 4.3.1 | Centering and shuttering including strutting, propping etc. and removal of form work for : Foundations, footings, bases for columns
|  | Foundation:PCC | 2 | 48 | 1.5 | 0.075 |  | 10.8 | sqm
|  | Column Shuttering | 2 | 48 | 0.45 | 1.2 |  | 51.84
|  | Ramp Area | 2 | 2 | 2 | 0.15 |  | 1.2
|  | Flooring Top Surface | 2 |  | 16.5 | 0.1 |  | 3.3
|  |  | 2 |  | 11.5 | 0.1 |  | 2.3
[6 empty] | Total Qty |  | 69.44 | sqm
6 | 5.1 | Providing and laying in position specified grade of reinforced cement concrete, excluding the cost of centering, shuttering, finishing and reinforcement - All work up to plinth level :
| 5.1.2 | 1:1.5:3 (1 cement : 1.5 coarse sand (zone-III) derived from natural sources : 3 graded stone aggregate 20 mm nominal size de rived from natural sources)
|  | Footing (1500x1500) | 2 | 12 | 1.5 | 1.5 | 0.3 | 16.2 | cum
|  | Column | 2 | 12 | 0.45 | 0.45 | 1.2 | 5.832
[6 empty] | Total Qty |  | 22.032 | cum
7 | 2.25 a) | Excavating, supplying and filling of local earth (including royalty) by mechanical transport upto a lead of 5km also including ramming and watering of the earth in layers not exceeding 20 cm in trenches, plinth, sides of foundation etc. complete
|  | Surface Area | 2 |  | 16.5 | 11.5 | 0.6 | 227.7 | cum
8 | 6.1 | Brick work with common burnt clay F.P.S. (non modular) bricks of class designation 7.5 in foundation and plinth in:
| 6.1.2 | Cement mortar 1:6 (1 cement : 6 coarse sand)
|  | Foundation: For closed the store(Below the Foundation) | 2 | 2 | 16.5 | 0.6 | 1 | 39.6 | cum
|  |  | 2 | 2 | 11.5 | 0.6 | 1 | 27.6
[8 empty] | 67.2 | cum
9 | 6.12 | Half brick masonry with common burnt clay F.P.S. (non modular) bricks of class designation 7.5 in foundations and plinth in
| 6.12.2 | cement mortar 1:4 (1 cement : 4 coarse sand)
|  | Above Foundation: For closed the store | 2 | 2 | 28 | 2 |  | 224 | sqm
10 | 13.1 | 12 mm cement plaster of mix :
| 13.1.2 | 1:6 (1 cement: 6 fine sand) | 2 | 2 | 28 | 2 |  | 224 | sqm
11 | 13.7 | 12 mm cement plaster finished with a floating coat of neat cement of mix
| 13.7.2 | 1:4 (1 cement: 4 fine sand | 2 | 1 | 16.5 | 11.5 |  | 379.5 | sqm
12 | 2.27 | Supplying and filling in plinth with sand under floors, including watering, ramming, consolidating and dressing complete.
|  | Flooring Top Surface | 2 |  | 16.5 | 11.5 |  | 379.5 | sqm
13 | 5.22.6 | Steel reinforcement for R.C.C. work including straightening, cutting, bending, placing in position and binding all complete upto plinth level. Thermo-Mechanically Treated bars of grade Fe-500D or more
|  | Raft Steel(1500x1500): 1500/150=10+1=11 No in one side so, as per Drawing bothways, Total No of Steel- 11x2x2= 44 nos, Total Length of steel= 1500+200+200 = 1900m and wt of steel= 1.9x0.61x44 Nos = 50.996 Kg in one raft. | 2 | 12 |  | 50.996 |  | 1223.904 | KG
|  | In Column: In Drawing showing 8Bar@16 Dia, Length-1.774x8x 1.58= 22.13 kg in one column | 2 | 12 |  | 22.13 |  | 531.12
|  | Striups: 8Dia@150C/C= 1200/150=8+1=9 Nos,Strips length- Column sixe 450x450 so Total Length= 1480+144=1624mm. Wt of one stirup in one column= 1.624x.39x9 = 5.70kg. | 2 | 12 |  | 5.7 |  | 136.8
[6 empty] | Total Qty |  | 1891.824 | kg
14 | 10.19 | Providing and fixing mild steel round holding down bolts with nuts and washer plates complete.
|  | Foundation Bolts : 4 Nos 20 Dia bolt-Length-1000mm | 12 | 4 |  |  |  | 48 | Nos
|  | weight of M20 bolt= 5.75kg for 1m Length |  | 48 |  |  | 5.75 | 276
[6 empty] | Total Qty |  | 276 | kg
15 | 12.5 | Providing and fixing precoated galvanised iron profile sheets (size, shape and pitch of corrugation as approved by Engineer-in-Charge) of total coated thickness 0.50 mm (base metal of minimum 0.45 mm thickness with total coating thickness of 0.05mm) with zinc coating 120 grams per sqm as per IS: 277, in 240 mpa steel grade, 5-7 microns epoxy primer on both side of the sheet and polyester top coat 15-18 microns. Sheet should have protective guard film of 25 microns minimum to avoid scratches during transportation and should be supplied in single length upto 12 metre or as desired by Engineer-in-charge. The sheet shall be fixed using self drilling /self tapping screws of size (5.5x 55 mm) with EPDM seal, complete upto any pitch in horizontal/ vertical or curved surfaces, excluding the cost of purlins, rafters and trusses and including cutting to size and shape wherever required
|  | Iron Profile Sheet | 2 | 15.6 | 10.6 |  |  | 330.72
|  |  | 2 | 2 | 15 | 5 |  | 300
|  |  | 2 | 2 | 10 | 5 |  | 200
|  | Ded (-) | -2 | 1 | 5.1 | 2.8 |  | -28.56
802.16
[6 empty] | Total Qty | Says | 802.16 | SQM
16 | 10.2 | Structural steel work riveted, bolted or welded in built up sections, trusses and framed work, including cutting, hoisting, fixing in position and applying a priming coat of approved steel primer all complete
| 1 | Columns(175 ISMB) | 2 | 10 | 4.56 |  |  | 91.2 | 19.6kg/m
|  | Divider(175 ISMB) | 2 | 4 | 10 |  |  | 80
|  |  | 2 | 3 | 15 |  |  | 90
261.2
5119.52
[5 empty] | A |  | Says | 2560
|  | Columns(ISMB 300) | 2 | 2 | 4.56 |  |  | 9.12 | 46 kg/m
9.12
419.52
[5 empty] | B | Says Total Weight |  | 419.52
| 3 | Divider (90x90x8 mm) | 2 | 4 | 11.25 |  |  | 90 | 10.8 kg /meter
|  | Principal raft (90*90*8 mm) | 2 | 4 | 10.64 |  |  | 85.12
|  | Ridge (90*90*8 mm) | 8 | 6 | 1 |  |  | 48
|  | Principal raft support (90*90*8 mm) | 8 | 1 | 3.85 |  |  | 30.8
253.92
2742.336
[5 empty] | C | Says Total Weight |  | 2742.336
| 4 | B Plate (350*350*12mm) | 2 | 12 | 1.47 |  | 11.54 | 276.96
| 5 | B Plate (300*300*12mm) | 2 | 12 | 1.47 |  | 11.54 | 276.96
| 6 | cleat 100*100*10 mm | 4 | 48 | 0.96 |  | 0.8 | 153.6
[6 empty] | Total Weight |  | 707.52
|  | Purlin- Zed | 2 | 37 | 5 |  |  | 370
|  |  | 2 | 12 | 15.6 |  |  | 374.4
[5 empty] | D | Total Qty |  | 744.4
4570.616
|  | Total Weight (a+b+c+d) | [5 empty] | 10999.992 | Kg
17 | 12.51.1 | Providing and fixing precoated galvanised steel sheet roofing accessories 0.50 mm (+0.05 %) total coated thickness, Zinc coating 120 grams per sqm as per IS: 277, in 240 mpa steel grade, 5-7 microns epoxy primer on both side of the sheet and polyester top coat 15-18 microns using self drilling/ self tapping screws complete : Ridges plain (500 - 600mm)
|  | Top | 2 | 1 | 15.3 |  |  | 30.6
|  | Sides | 2 | 4 | 5 |  |  | 40
[6 empty] | Total Qty |  | 70.6 | Meter
18 | 13.62.1 | Painting with synthetic enamel paint of approved brand and manufacture to give an even shade : Two or more coats on new work
|  | Prline Zed | 2 | 37 | 5 |  | 0.7 | 259
|  |  | 2 | 12 | 5 |  | 0.7 | 84
|  | ISME 300 | 2 | 2 | 4.5 |  | 1.16 | 20.88
|  | ISMB 175 | 2 | 10 | 4.5 |  | 0.63 | 56.7
|  | Base Plate Top & Bottom | 2 | 2 | 12 |  | 0.3 | 14.4
|  | Divider (90x90x8 mm) | 2 | 4 | 11.25 |  | 0.3616 | 32.544
|  | Principal raft (90*90*8 mm) | 2 | 4 | 10.64 |  | 0.3616 | 30.7794
|  | Ridge (90*90*8 mm) | 8 | 6 | 0.5 |  | 0.3616 | 8.6784
|  | Principal raft support (90*90*8 mm) | 8 | 7 | 0.3 |  | 0.3616 | 6.0749
|  | cleat 100*100*10 mm | 8 | 48 | 0.1 |  | 0.1 | 3.84
|  | MS Door shutter | 2 | 2 | 3 | 2 | 1.1 | 13.2
[6 empty] | Total Qty |  | 530.0967 | Sqm
19 | 10.6 | Supplying and fixing rolling shutters of approved make, made of required size M.S. laths, interlocked together through their entire length and jointed together at the end by end locks, mounted on specially designed pipe shaft with brackets, side guides and arrangements for inside and outside locking with push and pull operation complete, including the cost of providing and fixing necessary 27.5 cm long wire springs manufactured from high tensile steel wire of adequate strength conforming to IS: 4454 - part 1 and M.S. top cover of required thickness for rolling shutters.
| 10.6.1 | 80x1.25 mm M.S. laths with 1.25 mm thick top cover | 2 | 2 | 3 | 2 |  | 24 | sqm
| 10.7 | Providing and fixing ball bearing for rolling shutters | 2 | 2 |  |  |  | 4 | Nos
20 | 13.44 | Finishing walls with water proofing cement paint of required shade :
| 13.44.1 | New work (Two or more coats applied @ 3.84 kg/10 sqm) | 2 | 1 | 28 | 2 |  | 112 | Sqm

## MB-Electrical
Sr.No | DSR-2022 | Electricals Item | Unit | Qty
Part A: Total Schedule Items As Per DSR-2022
1 | 1.41 | Installation, testing and commissioning of pre-wired, fluorescent fitting/LED/ compact fluorescent fitting of all types, comlete with all accessories and tube etc. directly on celing/ wall, including connection with 1.5 Sq. mm FRLS PVC insulated, copper conductor, sigle core cable and | Each | 4
2 | 19.1 | Supply, Installation, Testing and Commissioning of 1200 mm sweep, BEE 5 star rated, ceiling fan with Brush Less Direct Current (BLDC) Motor, class of insulation: B, 3 nos. blades, 30 cm long down rod, 2 nos. canopies, shackle kit, safety rope, copper winding, Power Factor not less than 0.9, Service Value (CM/M/W) minimum 6.00, Air delivery minimum 210 Cum/Min , 350 RPM (tolerance as per IS : 374-2019), THD less than 10%, remote or electronic regulator unit for speed control and all remaining accessories including safety pin, nut bolts, washers, temperature rise=75 degree C (max.), insulation resistance more than 2 mega ohm, suitable for 230 V, 50 Hz, single phase AC Supply, earthing etc. complete as req | Each | 4
3 | 1.33 | Supplying and fixing 3 pin, 5 A ceiling rose on the existing junction box/ wooden block including connections etc. as required. | Each | 4
4 | 1.1 | Wiring for light point/ fan point/ exhaust fan point/ call bell point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface / recessed Medium duty PVC conduit , with modular switch, modular plate, suitable GI box and earthing the point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable etc. as required
| 1.10.1 | Group A | Point | 4
| 1.10.2 | Group B | Point | 4
5 | 1.14 | Wiring for circuit/ submain wiring alongwith earth wire with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface/ recessed medium class medium class PVC conduitas required .
| 1.14.2 | 2 X 2.5 sq. mm + 1 X 2.5 sq. mm earth wire | Metre | 20
| 1.14.3 | 2 X 4 sq. mm + 1 X 4 sq. mm earth wire | Metre | 20
6 | 1.24 | Supplying and fixing following modular switch/ socket on the existing modular plate & switch box including connections but excluding modular plate etc. as required
| 1.24.1 | 5/6 A switch | Each | 4
| 1.24.3 | 15/16 A switch | Each | 4
| 1.24.4 | 3 pin 5/6 A socket outlet | Each | 4
| 1.24.5 | 6 pin 15/16 A socket outlet | Each | 4
7 | 1.25 | Supplying and fixing two module stepped type electronic fan regulator on the existing modular plate switch box including connections but excluding modular plate etc. as required. | Each | 4
8 | 1.27 | Supplying and fixing following size/ modules, GI box alongwith modular base & cover plate for modular switches in recess etc. as required
| 1.27.2 | 3 Module | Each | 4
9 | 2.12 | Supplying and fixing following rating, double pole, 240 V, isolator in the existing MCB DB complete with connections,testing and commissioning etc. as required
| 2.12.1 | 40 A | Each | 1
10 | 2.3 | Supplying and fixing following way, single pole and neutral, sheet steel, MCB distribution board, 240 V, on surface/ recess,complete with tinned copper bus bar, neutral bus bar, earth bar,din bar, interconnections, powder painted including earthing etc.as required. (But without
| 2.3.1 | 6 way, Double door | Each | 1

## BOQ
POWER GRID CORPORATION OF INDIA LTD 765/400/220 KV BHADLA-2 SUB STATION
Name Of Work : : Fabrication of 2-Nos Closed Store shed for Oil Drums at Bhadla-2 Substation
S.No. | DSR 2023 Item No | Description | Unit | Quantity | Rate | Amount
Schedule Items-Civil
1 | 2.28 | Surface dressing of the ground including removing vegetation and inequalities not exceeding 15 cm deep and disposal of rubbish, lead up to 50 m and lift up to 1.5 m. All kinds of soil | SQM | 544.5 |  | 0
2 | 2.8.1 | Earth work in excavation by mechanical means (Hydraulic excavator) / manual means in foundation trenches or drains (not exceeding 1.5 m in width or 10 sqm on plan), including dressing of sides and ramming of bottoms, lift upto 1.5 m, including getting out the excavated soil and disposal of surplus excavated soil as directed, within a lead of 50 m. All kinds of soil. | CUM | 109.512 |  | 0
3 | 2.25 | Filling available excavated earth (excluding rock) in trenches, plinth, sides of foundations etc. in layers not exceeding 20cm in depth, consolidating each deposited layer by ramming and watering, lead up to 50 m and lift upto 1.5 m. | CUM | 87.48 |  | 0
4 | 4.1.8 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering - All work up to plinth level : 1:4:8 (1 Cement : 4 coarse sand (zone-III) derived from natural sources : 8 graded stone aggregate 40 mm nominal size derived from natural sources) | CUM | 63.0255 |  | 0
5 | 4.3.1 | Centering and shuttering including strutting, propping etc. and removal of form work for : Foundations, footings, bases for columns | SQM | 69.44 |  | 0
6 | 5.1 | Providing and laying in position specified grade of reinforced cement concrete, excluding the cost of centering, shuttering, finishing and reinforcement - All work up to plinth level :
| 5.1.2 | 1:1.5:3 (1 cement : 1.5 coarse sand (zone-III) derived from natural sources : 3 graded stone aggregate 20 mm nominal size de rived from natural sources) | CUM | 22.032 |  | 0
7 | 2.25 a) | Excavating, supplying and filling of local earth (including royalty) by mechanical transport upto a lead of 5km also including ramming and watering of the earth in layers not exceeding 20 cm in trenches, plinth, sides of foundation etc. complete | CUM | 227.7 |  | 0
8 | 6.1 | Brick work with common burnt clay F.P.S. (non modular) bricks of class designation 7.5 in foundation and plinth in: |  |  |  | 0
| 6.1.2 | Cement mortar 1:6 (1 cement : 6 coarse sand) | CUM | 67.2 |  | 0
9 | 6.12 | Half brick masonry with common burnt clay F.P.S. (non modular) bricks of class designation 7.5 in foundations and plinth in |  |  |  | 0
| 6.12.2 | cement mortar 1:4 (1 cement : 4 coarse sand) | SQM | 224 |  | 0
10 | 13.1 | 12 mm cement plaster of mix : |  |  |  | 0
| 13.1.2 | 1:6 (1 cement: 6 fine sand) | SQM | 224 |  | 0
11 | 13.7 | 12 mm cement plaster finished with a floating coat of neat cement of mix |  |  |  | 0
| 13.7.2 | 1:4 (1 cement: 4 fine sand | SQM | 379.5 |  | 0
12 | 2.27 | Supplying and filling in plinth with sand under floors, including watering, ramming, consolidating and dressing complete. | SQM | 379.5 |  | 0
13 | 5.22.6 | Steel reinforcement for R.C.C. work including straightening, cutting, bending, placing in position and binding all complete upto plinth level. Thermo-Mechanically Treated bars of grade Fe-500D or more | KG | 1891.824 |  | 0
14 | 10.19 | Providing and fixing mild steel round holding down bolts with nuts and washer plates complete. | KG | 276 |  | 0
15 | 12.5 | Providing and fixing precoated galvanised iron profile sheets (size, shape and pitch of corrugation as approved by Engineer-in-Charge) of total coated thickness 0.50 mm (base metal of minimum 0.45 mm thickness with total coating thickness of 0.05mm) with zinc coating 120 grams per sqm as per IS: 277, in 240 mpa steel grade, 5-7 microns epoxy primer on both side of the sheet and polyester top coat 15-18 microns. Sheet should have protective guard film of 25 microns minimum to avoid scratches during transportation and should be supplied in single length upto 12 metre or as desired by Engineer-in-charge. The sheet shall be fixed using self drilling /self tapping screws of size (5.5x 55 mm) with EPDM seal, complete upto any pitch in horizontal/ vertical or curved surfaces, excluding the cost of purlins, rafters and trusses and including cutting to size and shape wherever required | SQM | 802.16 |  | 0
16 | 10.2 | Structural steel work riveted, bolted or welded in built up sections, trusses and framed work, including cutting, hoisting, fixing in position and applying a priming coat of approved steel primer all complete | KG | 10999.992 |  | 0
17 | 12.51.1 | Providing and fixing precoated galvanised steel sheet roofing accessories 0.50 mm (+0.05 %) total coated thickness, Zinc coating 120 grams per sqm as per IS: 277, in 240 mpa steel grade, 5-7 microns epoxy primer on both side of the sheet and polyester top coat 15-18 microns using self drilling/ self tapping screws complete : Ridges plain (500 - 600mm) | Metre | 70.6 |  | 0
18 | 13.62.1 | Painting with synthetic enamel paint of approved brand and manufacture to give an even shade : Two or more coats on new work | SQM | 530.0967 |  | 0
19 | 10.6 | Supplying and fixing rolling shutters of approved make, made of required size M.S. laths, interlocked together through their entire length and jointed together at the end by end locks, mounted on specially designed pipe shaft with brackets, side guides and arrangements for inside and outside locking with push and pull operation complete, including the cost of providing and fixing necessary 27.5 cm long wire springs manufactured from high tensile steel wire of adequate strength conforming to IS: 4454 - part 1 and M.S. top cover of required thickness for rolling shutters. |  |  |  | 0
| 10.6.1 | 80x1.25 mm M.S. laths with 1.25 mm thick top cover | SQM | 24 |  | 0
20 | 10.7 | Providing and fixing ball bearing for rolling shutters | Nos | 4 |  | 0
21 | 13.44 | Finishing walls with water proofing cement paint of required shade : |  |  |  | 0
| 13.44.1 | New work (Two or more coats applied @ 3.84 kg/10 sqm) | SQM | 112 |  | 0
|  | Electricals Item |  |  |  | 0
|  | Part A: Total Schedule Items As Per DSR-2022 |  |  |  | 0
1 | 1.41 | Installation, testing and commissioning of pre-wired, fluorescent fitting/LED/ compact fluorescent fitting of all types, comlete with all accessories and tube etc. directly on celing/ wall, including connection with 1.5 Sq. mm FRLS PVC insulated, copper conductor, sigle core cable and | Each | 4 |  | 0
2 | 19.1 | Supply, Installation, Testing and Commissioning of 1200 mm sweep, BEE 5 star rated, ceiling fan with Brush Less Direct Current (BLDC) Motor, class of insulation: B, 3 nos. blades, 30 cm long down rod, 2 nos. canopies, shackle kit, safety rope, copper winding, Power Factor not less than 0.9, Service Value (CM/M/W) minimum 6.00, Air delivery minimum 210 Cum/Min , 350 RPM (tolerance as per IS : 374-2019), THD less than 10%, remote or electronic regulator unit for speed control and all remaining accessories including safety pin, nut bolts, washers, temperature rise=75 degree C (max.), insulation resistance more than 2 mega ohm, suitable for 230 V, 50 Hz, single phase AC Supply, earthing etc. complete as req | Each | 4 |  | 0
3 | 1.33 | Supplying and fixing 3 pin, 5 A ceiling rose on the existing junction box/ wooden block including connections etc. as required. | Each | 4 |  | 0
4 | 1.1 | Wiring for light point/ fan point/ exhaust fan point/ call bell point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable in surface / recessed Medium duty PVC conduit , with modular switch, modular plate, suitable GI box and earthing the point with 1.5 sq.mm FRLS PVC insulated copper conductor single core cable etc. as required |  |  |  | 0
| 1.10.1 | Group A | Point | 4 |  | 0
| 1.10.2 | Group B | Point | 4 |  | 0
5 | 1.14 | Wiring for circuit/ submain wiring alongwith earth wire with the following sizes of FRLS PVC insulated copper conductor, single core cable in surface/ recessed medium class medium class PVC conduitas required . |  |  |  | 0
| 1.14.2 | 2 X 2.5 sq. mm + 1 X 2.5 sq. mm earth wire | Metre | 20 |  | 0
| 1.14.3 | 2 X 4 sq. mm + 1 X 4 sq. mm earth wire | Metre | 20 |  | 0
6 | 1.24 | Supplying and fixing following modular switch/ socket on the existing modular plate & switch box including connections but excluding modular plate etc. as required |  |  |  | 0
| 1.24.1 | 5/6 A switch | Each | 4 |  | 0
| 1.24.3 | 15/16 A switch | Each | 4 |  | 0
| 1.24.4 | 3 pin 5/6 A socket outlet | Each | 4 |  | 0
| 1.24.5 | 6 pin 15/16 A socket outlet | Each | 4 |  | 0
7 | 1.25 | Supplying and fixing two module stepped type electronic fan regulator on the existing modular plate switch box including connections but excluding modular plate etc. as required. | Each | 4 |  | 0
8 | 1.27 | Supplying and fixing following size/ modules, GI box alongwith modular base & cover plate for modular switches in recess etc. as required |  |  |  | 0
| 1.27.2 | 3 Module | Each | 4 |  | 0
9 | 2.12 | Supplying and fixing following rating, double pole, 240 V, isolator in the existing MCB DB complete with connections,testing and commissioning etc. as required |  |  |  | 0
| 2.12.1 | 40 A | Each | 1 |  | 0
10 | 2.3 | Supplying and fixing following way, single pole and neutral, sheet steel, MCB distribution board, 240 V, on surface/ recess,complete with tinned copper bus bar, neutral bus bar, earth bar,din bar, interconnections, powder painted including earthing etc.as required. (But without |  |  |  | 0
| 2.3.1 | 6 way, Double door | Each | 1 |  | 0