| Sr. No | Section/Clause Reference | Bidders Queries | POWERGRID Reply |
| --- | --- | --- | --- |
| 1 | NA | Package OH01 comprises multiple transmission lines under the same package, each having its own line-specific sag-tension requirements. We understand that only one HTLS conductor design is to be offered where multiple sag-tension conditions are specified for a particular voltage level. However, it is not clear whether the bidder is permitted to offer different HTLS conductor designs for different transmission lines within the same package, where each proposed conductor fully complies with the respective technical and sag-tension requirements of the corresponding transmission line. It is requested to kindly clarify whether different HTLS conductor designs may be offered for different transmission lines under Package OH01, or whether a single HTLS conductor design is mandatory for all transmission lines falling under the same voltage level within the package. | Bidder to refer clause 1.4, Section-IA of Technical specification. The Provision of bidding documents shall prevail. |
| 2 | NA | Bidder is India's leading integrated power transmission developer and solutions provider, focused on addressing complex challenges in the sector by tackling the key constraints of time, space and capital. We refer to the above-mentioned tender and wish to convey our sincere appreciation for the opportunity to participate in this prestigious project. Our company is keenly interested in submitting a technically responsive and commercially competitive bid. During our detailed review of the tender specification, we noted that ASTM has recently published ASTM B1012 – Standard for Shaped Wire Compact Concentric-Lay-Stranded Aluminium Conductors, Carbon Fiber Composite Supported (ACCFCS/TW), which establishes the internationally recognized requirements for the complete ACCFCS/TW conductor. ASTM B1012 governs the complete conductor & so is the applicable international standard for the complete ACCFCS/TW conductor, while ASTM B987-25 specifies the requirements and Design Validation Tests for the polymer matrix composite (PMC) core. The refined HTLS conductor and its associated core shall comply with the applicable published national and/or international standards. Accordingly, we request that the specification explicitly provides that: •The offered HTLS conductor shall comply with ASTM B1012 (or an equivalent applicable national/international standard) covering the complete conductor. •The offered PMC core shall comply with ASTM B987-25, including successful completion of all Design Validation Tests specified in Table 2. Thus, as a bidder, we understand that, during technical evaluation, PGCIL will evaluate compliance of the offered PMC core fully tested against the Design Validation Tests prescribed in Table 2 of ASTM B987-25. Further, wherever the PMC core is part of the offered HTLS complete covered core shall also be required to have successfully passed the same Design Validation Tests specified in Table 2 of ASTM B987-25. It is also our understanding that the metallic covering, where applicable, shall comply with the standards specified under Clause 2.14 (Standards) of Volume II, Section VIII (HTLS Conductor) Pg No 18 of 29. We believe this approach is fully aligned with the intent of the CEA guidelines/advisories, which emphasize adherence of all PMC cores to recognized national or international standards. We shall be grateful if you could kindly confirm whether the above understanding is in line with PGCIL’s intended technical requirements. Such clarification will ensure uniform interpretation of the specification by all prospective bidders and facilitate submission of technically compliant offers. Furthermore, in view of the recent publication of ASTM B1012 and the need for bidders to comprehensively evaluate its technical implications, we respectfully request an extension of the bid submission deadline by two weeks. The requested extension will enable all prospective bidders to incorporate the latest international standard in their technical evaluation, thereby enhancing competitiveness and ensuring complete compliance with the Employer's requirements. We trust that our request will receive your kind consideration. Bidder remains committed to supporting PGCIL with innovative, reliable and internationally compliant HTLS conductor solutions, and we look forward to participating in the successful execution of this important project. | Bidder may refer clause 1.9.2 of SECTION-VIIB of Technical specification (VOLUME-II) wherein it is specified that..." In case of Polymer Matrix Composite (PMC) core, offered core design shall meet the provisions of ASTM B987-25". In this regard, it is clarified that the provisions of ASTM B987 includes design validation tests. |