## Queries
Clarification No. 3
85MW Nagda, MP
SPECIFICATION NO.: CC/NT/W-MISC/DOM/A02/23/01366/Rfx-5002002681
Sl. No | Clause No./ Drg.No. | Description as per Tender Specification | Query | Employer's reply
1 | --- | --- | We are in receipt of latest Amendment No. -3 issued yesterday, 09th May, 2023.We intend to participate in the subject tender. However, the latest amendment regarding alignment to the “Report of the Working Group in respect of Data Submission Procedure and Verification of Compliance to CEA Regulations on Technical Standards for Connectivity to the Grid by RE Generators July 2022” requires certain additional technical clarifications from PGCIL. We request you to please review our below submission and respond at the earliest so that we can participate in the Tender. 1. According to the provisions of Bidding Documents, only linear method is followed in the PG test procedure which is compliant under the following conditions like Unity Power Factor and 1 PU at Inverter Terminal. The First Year Energy of 178 MU is committed on following conditions like Unity power factor and 1 PU at inverter terminal. In view of the latest amendment issued yesterday, the grid disturbance like Power factor, 0.95 PU, LVRT & HVRT functions etc. which will compensate on real power cannot be captured /measured at the meter. Hence a suitable correction factor or a different PG test methodology has to be mutually agreed to measure the committed energy during PG Test and as well as to measure the Annual Generation during O&M Period. PGCIL to confirm to drop the Liner method and accept the Mutually agreed methodology to measure the energy during PG test as well as to measure Annual generation during O&M Period. 2. As per the Working Group Report inverters are allowed for meeting the CEA Standards. Accordingly, we have considered additional inverter capacity to comply with the requirements of the Working Group Report. We will not be providing any other equipment such as STATCOM, Capacitor banks etc. to meet the CEA Standards. We request PGCIL to review above and confirm. | Bidder shall quote as per provisions of bidding documents.
2 | --- | --- | Additionally, in order to arrange the necessary internal approvals for Bidding towards the tender we request PGCIL to please extend the bid submission date till 18th May 2023. We request PGCIl to consider our above submissions favourably and oblige. | Presently, bid submission has been extended till 16.05.2023.