| Sl. No. | Clause ref | Existing clause | Queries asked by the bidder | POWERGRID’s clarification |
| --- | --- | --- | --- | --- |
|  | Table 2.1, Sec-IVD, Technical Specifications | Ultimate bond between Steel & Rock for Hard Rock foundations KN/M2 (Kg/M2) 0.147 (15) | Ultimate bond stress between steel and rock for hard rock foundations given in table. We feel that it is a typo error; it should be bond stress between steel anchors and grout material. Please confirm our understanding is correct. | Refer Amendment No-3. |
|  |  |  | Values for bond stress between steel anchors and grout given as 15 kg/M2. We feel that it is a typo error; it should be 15 kg/CM2. Please confirm our understanding is correct. | Refer Amendment No-3. |
|  |  | - | Values of Bond stress between Hard rock & concrete and Hard rock & Grout not given in the specification. Bidder can use the bond stress values as available in annexure-IV, chapter-10 of CBIP manual, publication no. 323. Please Confirm. | Refer Amendment No-3. |
|  | Clause No. 1.3, Section IA Technical Specifications | (i) Tension at 32°C and full wind condition: • ≤ 11421 kg corresponding to wind pressure of [77.19 X Gust Factor] kg/sqm as per IS802 and not exceeding 70% of UTS of proposed conductor. (i) Tension at designed maximum temperature and full wind condition: • ≤ 11421 kg corresponding to wind pressure of [77.19 X Gust Factor] kg/sqm as per IS802 and not exceeding 70% of UTS of proposed conductor. | Request for Clarification: • Calculation of Wind Pressure as per Wind Zone=3, Terrain Category=2, Reliability level=2 as per IS-802 comes out to be 757 N/sqm (i.e. 77.2 kg/sqm) instead of 130.45 kg/sqm. • Kindly Clarify whether [77.2 X Gust Factor] kg/sqm needs to be utilized for working out Sag Tension calculation of HTLS Conductor for Multi Ckt Towers OR [130.45 X Gust Factor] kg/sqm needs to be used. | For revised Calculation of Wind Pressure pls refer Amendment No-1. |
|  | Clause No. 1.9.2 Section VII B Technical Specifications | However, in no case, the guaranteed values for torsion & elongation of Steel/Invar core of the offered HTLS Conductor shall be less than as indicated below: - Minimum No. of twists in gauge length equal to 100 times the dia. of wire which the strand can withstand in the torsion test (before stranding) *=12 - *A reduction of 2 number of twists is permitted for after stranding values. | Request for Amendment: • We request PGCIL to use latest IEC-63248 standard read as ‘Conductors for overhead lines-Coated or cladded metallic wire for concentric lay stranded conductor’ for guaranteed values of Torsion and Elongation of Steel core of the offered HTLS Conductor | Bidding Document to prevail. |
|  | Sch-1, Sch-2 of BPS-Rev-01 | Sr. No. 69 to 78, “Tower Quantity for SOR” | Under this item, the bidder was asked to quote for tower tonnage for Multicircuit towers and whereas in the same package the bidder was asked to quote for 400kV M/C (Twin HTLS) narrow base towers including design. Please clarify what is meant by “Tower Quantity for SOR” and whether both the Multicircuit towers are same or different. Kindly Clarify? | Bidder to quote for 400kV M/C (Twin HTLS) narrow base towers including design. Quantities mentioned under “Tower Quantity for SOR” is deleted. Refer Amendment-II. |
|  | Sch-3 of BPS-Rev-01 | Sr. No. 9 to 40, “WORK ASSOCIATED WITH FOUNDATION” | As per this item, the foundation has to be designed considering the soil properties of Gujarat State only, eventhough the line terminates at Dadra Nagar haveli UT for which the soil properties are not provided. Kindly confirm. | Soil properties of Gujarat State may be considered for foundation design in Dadra Nagar haveli UT. |
|  | Cl 2.4, Sec-IA of Technical specification | M/C portion (Part-II) of 400 kV D/C (twin HTLS) Navsari (New) (south Gujarat) - Kala transmission line and 400 KV D/C (twin HTLS) Navsari (New) (south Gujarat)- Magarwada transmission line covered under the subject package shall be designed with Narrow base having base width i.e. centre to centre of tower legs of +9M extension shall be kept as 10 to 14m. | As per our understanding, for Narrow base Multi circuit towers all the towers can be designed with base width at +9m extension between 10m to 14m and there is no individual tower wise base width restriction. Please confirm our understanding is correct. | Bidder’s understanding is correct. |
|  | BPS & Technical specification | -- | While going through the tender documents, we have not found following information in the specification which are required to carry out the monopole foundation design. - Maximum depth of pole foundation not provided. - Type of soil for pole foundation not provided. Please provide the same at the earliest. | Requirement of Monopole is deleted from the scope. Refer amendment No-1. |
|  | Sch-3 BPS & Technical specification | Navasari-Magarwada-Kala Detailed survey including route alignment, profiling and tower spotting: 52.39kms 400 KV Banaskantha - Sankhari D/c line Detailed survey including route alignment, profiling and tower spotting:22.5kms | Google earth route length is coming 400 Km- Kindly Confirm Google earth route length is coming 80 Km-Kindly Confirm Aside this, please note without getting the proper coordinates of end point & Start point, it is difficult to carry out the WOS. Once again you are requested to arrange required coordinate to carry out the proper WOS. | Route length as per bidding document to prevail. Please refer Section-XII: FAQ of Technical specification regarding co-ordinates for starting point, terminating point and all angle points of the line |