| Sl. No. | Clause ref | Existing clause | Queries asked by the bidder | POWERGRID’s clarification |
| --- | --- | --- | --- | --- |
|  | Section-IVA Clause1.4.9 Tower Loading condition | 1.4.9 - Tower Loading condition. | Kindly confirm following formula to be used on wind on tower for Oblique wind : - Fwt,Trans = Pd* (1 + 0.2 sin²2θ) (AeT*CdtT*cosθ)*GT Fwt Long = Pd *(1 + 0.2 sin²2θ) (AeL*CdtL*sinθ)*GT | Confirmed |
|  | Volume II / Section IVA/ Tower design/clause No.1.2.3 and /Section 1A/Scope/Clause No. 1.4.2 |  | As per tower design clause 1.2.3, For 400kV and above voltage level lines, the B/DB, C/DC, and D/DD towers shall be designed for providing unequal leg extensions from -3.0m/-1.5m/+0m/ +1.5m/ +3.0m/+4.5m/ +6.0m/ +7.5m/ +9.0m with maximum difference between the shortest and the longest leg of 3m. As per Volume II /Section 1A/ cl 1.4.2, line passes through plain and coastal area. As per our understanding, design with un-equal leg extensions are not required for D/C Narrow base tension towers as the line is passing through plain area. Kindly confirm and accordingly revise the price schedule | As per clause 1.2.3 of section-IVA of technical specification, For 400kV and above voltage level lines, the B/DB, C/DC, and D/DD towers shall be designed for providing unequal leg extensions from -3.0m/-1.5m/+0m/ +1.5m/ +3.0m/+4.5m/ +6.0m/ +7.5m/ +9.0m with maximum difference between the shortest and the longest leg of 3m. |
|  | Volume II/Section 1A/Scope/Clause No. 1.4.2 | 1.4.2 Location Details and Terminal Points A | As per the clause, we understand that the fabricated tower parts and stubs shall have a zinc coating for Line-1 ( Coastal area) is 900gm/sqm and Line-2 (Plain area) 610 gm/sqm. Kindy confirm our understanding is correct. | Bidders understanding is correct. |