| Sr. No. | Clause No. & Reference | Tender Description | Bidders Query | POWERGRID Reply |
| --- | --- | --- | --- | --- |
|  | SBD Part-1 | Address for Correspondence | Employer is: POWERGRID Energy Services Limited (PESL) & PESL, a wholly owned subsidiary of Power Grid Corporation of India Ltd (POWERGRID). As we understand all the bidding forms (Form-1 to Form-23) is required to submit in the name of To: Power Grid Corporation of India Ltd. “Saudamini”, Plot No.2, Sector-29, Gurgaon, Haryana - 122 001 Kindly Confirm the same | Bidder’s understanding is correct. |
|  | SBD Part-1, Form 16 | Form 16 (Format for Price Adjustment Data) | Name of Material***; Price quoted by bidder at the time of bid submission*; Price as on XX days prior to date of shipment*; Variation*. ACSR conductor; NA**; NA**. Power Transformer (aluminum wound); NA**; NA**. Power Transformer (Copper wound). Distribution Transformer (aluminum wound). Distribution Transformer (Copper wound). Cables; NA**; NA**. *Detailed calculations as per Appendix-2 of Form 5 to be enclosed As per Part-3 (Price Adjustment Clause), price variation is applicable for STP,switchgear,Circuit breaker,& Isolator but in Part-1 (Form 16) price veriation is applicable only below mentioned items. 1.ACSR conductor 2. Power Transformer (aluminum wound) 3. Power Transformer (Copper wound) 4. Distribution Transformer (aluminum wound) 5. Distribution Transformer (Copper wound) 6. Cables Hence, you are requested to ammend the Form-16. | Provisions of the bidding documents shall remain unchanged. |
|  | Common BOQ of RDSS tender | Scope of work is distributed in Padum (3699 Mtr), Chazar (3486 Mtr), Phey (3189 Mtr), Cha (5994 Mtr) and Zankar Region (6000 Mtr. Avg) | There are different altitude in these five location which will affect the cost oif the materials and installtion work also. Hence we are requesting you to issue us locationwise BOQ so that exact cost should be calculated. | BOQ shall be followed. Bidder to quote accordingly. |
|  | Construction of 4 No. 33/11KV Substation | Substaion work is located in Padum(3699 Mtr.), Chazar(3486 Mtr.), Phey(3189 Mtr.), Cha(5994 Mtr.) | Kindly provide the GPS coordinates of these location so that we can identify for site visit and also provide the concern person's name and mobile no. | GPS Co-ordinates are as below:- 33/11 kV Padum station – 33.49463⁰ 76.822491⁰ 33/11 kV Chazar station – 33.61514⁰, 77.00592⁰ 33/11 kV Phey station – 33.24341⁰, 77.13680⁰ 33/11 kV Cha station - 33⁰14’36.3N 77⁰08’12.5E Power Grid Contact person – Surinder Kumar, DGM (9501102069) |
|  | Section-III_SBD Part 2 Page-183 BOQ Item nos: 41, 54, 75, 77, 93, 109, 141, 160, 179, 198, 217, 244 |  | As per TS, the STP is mentioned as "540 MPA" but in BOQ the same are mentioned as "410 MPA". Kindly confirm which one should be followed. If it is "410 MPA" , then provide the Technical Specification. | STP shall be 410 MPa as mentioned in BOQ. Refer SBD TS, Section Project clause 2.2.6 & IS 2713 for further details. |
|  | Section-III_SBD Part 2 Page: 502-513 | Technical Specification of Isolator. | As per supplier's concern, kindly confirm the Ice coating thickness on Isolator Contacts to calculate the exact cost of the material. | Refer clause no – 2.3 of Section projects. Equipment shall be suitable for service conditions as per clause no – 2.3 of section projects. Type test shall be followed as per SBD TS. |
|  | Section-VI_TS_33kV & 11kV Indoor switchgear-GIS | TECHNICAL SPECIFICATION FOR 33kV & 11kV Indoor Switchgear (GIS Type) | Due to high altitude (specially for Cha), maximum reputed vendors are refusing to share their offer. Kindly suggest. | The equipment shall be suitable for higher altitude in line with provisions of applicable standards. Higher voltage level equipment may be offered, where ever rated voltage equipment doesn’t meet the BIL requirement. |
|  | Section-I_Section Project page-21 |  | The SLD for substations with 1 incomer is not clearly visible. Please provide us the new SLD with clear view. | SLD with 1 incomer is attached herewith under file name “SLD with 1 Incomer” |
|  | Section-III_SBD Part 2 Page: 614 |  | Heat shrinkable insulating tubes are mentioned in the technical specification of the termination kit. However, based on our experience and supplier's concern, cold shrink kits are suitable due to the height and temperature. Kindly recheck and confirm what sholud we consider? | Shall be quoted as per TS. |