| Sr. No. | Clause No. & Reference | Tender Description | Bidders Query | POWERGRID Reply |
| --- | --- | --- | --- | --- |
|  | Section - II_SBD Part - 2 Scope of work, page no 52/250 and BOQ Sl.no- 57 | Technical documents & BOQ | As per scope of work, Stay Set consists with 50x8 mm stay clamp, guy insulator (2Nos.), anchor plate (300x300x8mm), nut-bolts, 2 Nos turn-buckles, 1.8 m long, 20 mm diameter solid GS stay- rod. Whereas in BOQ, stay set consists of 1 no anchor plate, 1 no anchor rod, turn buckle-1no, thimbles-2nos, guy strips-4nos, fastners to connect anchor plate to anchor rod for complete set. Kindly confirm the requirement. | BOQ shall be followed |
|  | BOQ Sl.no-60 | Technical documents & BOQ | As per supply schedule for 33KV line works: ACSR DOG on DP, for guarding arrangement 8 SWG GI wire mentioned but 10 SWG for cross lacing is not mentioned. Kindly clarify the requirement. | 8 SWG GI wire shall be used for lacing |
|  | Section - IV_LT AB Cable TS, page no 01/10 | Technical documents & BOQ | In supply schedule for LT reconductoring works, requirement of LT AB cable is 3CX50+1CX35 sq mm, 3CX70+1CX50 sq mm & 3CX120+1CX95 sq whereas in TS the designation of LT AB cable is 3Cx50+1Cx35+1Cx16sq mm, 3Cx70+1Cx50+1Cx16sq mm & 3Cx120+1Cx95+1Cx16sq mm respectively. kindly confirm the requirement. | BOQ shall be followed |
|  | Section - III_SBD Part - 2 Technical Specification | Technical documents & BOQ | Kinly provide technical specification of 1.1KV 4core 35mm2 & 1.1KV 1core 25mm2 unarmoured XLPE cable. | SBD Part-2 Technical Specification may be referred for TS of LT XLPE cable. |
|  | Section - III_SBD Part - 2 Technical Specification | Technical documents & BOQ | Kindly provide technical specification of 1.1 KV, FRLS, PVC cables of size 1CX70 sqmm, 1CX95 sqmm, 1CX185sqmm & 1CX240sqmm. | Referred cables shall be Aluminium/Unarmoured. For technical specification of 1.1KV 1Cx70, 1CX95 & 1CX185 Sq mm, FRLS, PVC cable refer Clause 3.3 of Section -Project of Bidding documents which is reproduced below: In case specification of any equipment/material is not included in this volume, the same shall be supplied as per relevant standards. Latest REC specification & Construction Standards may also be referred to. |
|  | Section - III_SBD Part - 2 Technical Specification | Technical documents & BOQ | Kindly provide the technical specification of 11KV HG fuse incl. all accessories. | For technical specification of 11 kV HG fuse refer Clause 3.3 of Section -Project of Bidding documents which is reproduced below: In case specification of any equipment/material is not included in this volume, the same shall be supplied as per relevant standards. Latest REC specification & Construction Standards may also be referred to. |
|  | Section - III_SBD Part - 2 Technical Specification | Technical documents & BOQ | Kindly provide technical specification of LT distribution box suitable for 250 KVA DT & 400 KVA DT. | For general construction, refer SBD Part-2, Technical Specifications for 63,100, 200 & 315 kVA LT Distribution Box. Further Cl no 2.2.3.8 of section project may be referred for detail of incomer and outgoing feeders. |
|  |  | Technical documents & BOQ | For DT works consumption of ACSR conductor is not considered in supply schedule. The same shall be claimed as per the line item provided in the substation ACSR conductor schedule. Kindly confirm. | ACSR DOG conductor is being used in 11 kV reconductoring works (mentioned in BOQ). Same conductor shall be used for DT connections. |
|  | SBD Part-3, Appendix-2 Price Adjustment | Appendix-2 Price Adjustment | Steel Tubular pole Price adjustment formula has 13% of Zinc where as we are not using the galvanised pole. Please check & revert how we use the formula of PV in steel tubular pole. | Refer Amendment-I enclosed herewith |
|  | SBD Part-3, Appendix-2 Price Adjustment | Appendix-2 Price Adjustment | In Steel tubular pole formula there is IS0 which is HR coil and the rate will be consider one month earlier from the date of tendering where as in example it was given below: if date of tendering falls in May 2022, the applicable prices of HR Coil (IS0) should be for the month March 2022 i.e. two month earlier from the date of tendering. Please clarify the same. | Refer Amendment-I enclosed herewith |
|  | General | -- | Please clarify whether BOCW is applicable for service contract or total contract price. | Bidder have to comply with all the statutory requirements. |
|  | SBD- Part-3 Appendix-1 TERMS AND PROCEDURES OF PAYMENT | 2. Progressive payments (Supply of Plant): 2.2. Second Installment (30%): | Existing Clause: Submission of certificate on measurement book by Project Manager that materials under consideration have been erected, tested and commissioned as per technical specification, scope of work & approved drawings. Since this 2nd stage of already supplied material. Payment shall not be linked to testing and commissioning. Else, it will have huge adverse impact on the cash flows. Please amended condition can be " Submission of certificate on measurement book by Project Manager that materials under consideration have been erected as per technical specification, scope of work & approved drawings. | Provisions of the bidding documents shall prevail and remain unchanged. |
|  | SBD- Part-3 Appendix-1 TERMS AND PROCEDURES OF PAYMENT | 3. Progressive payments (Erection): 3.2. Second and Final Installment (10%): | Existing Clause: Ninety percent (90%) payments against Erection contracts shall be paid on erection, testing and commissioning of works and on submission of relevant documents indicated herein under Since this 2nd stage of already supplied material. Payment shall not be linked to testing and commissioning. Else, it will have huge adverse impact on the cash flows. Please amended condition can be " Submission of certificate on measurement book by Project Manager that materials under consideration have been erected as per technical specification, scope of work & approved drawings. | Provisions of the bidding documents shall prevail and remain unchanged. |
|  | SBD- Part-1 Section - 1: Request for Bids Notice/Notice Inviting Tender | EMD/ Bid Security | EMD – An EMD of Rs. Bid Security of Rs. 2,38,62,000 (Indian Rupees Two Crores Thirty-Eight Lakh Sixty-Two Thousand Only) has been sought from the prospective bidders. We would request for a “Bid Securing Declaration” in place of EMD. | Provisions of the bidding documents shall prevail and remain unchanged. |
|  | SBD- Part-1 Section - 1: Request for Bids Notice/Notice Inviting Tender | Performance Security | The Performance Security amount is 10% of the Contract Price – RDSS Project by NTPC in the same region (Refer. NTPC Tender Document, NTPC/Consultancy/9900276378) in J&K, RAISI restricted PBG as 3%, whereas POWERGRID is asking for 10% Performance Security. We would request for “PBG of 3%” in place of 10%. | Provisions of the bidding documents shall prevail and remain unchanged. |