| Sl. No. | Clause Reference | Existing Provision | Amended Provision |
| --- | --- | --- | --- |
| Volume-II; Technical Specifications (Doc. Code No. DC- 4120-16857, April 2021) |  |  |  |
| 1 | Volume II, Section I, Clause 3, Sl. No. C 4 iv) | Tension at 2.5°C and 2/3 wind condition (32 kg/m2 wind pressure); ≤ 4474 kg & not exceeding 70% of UTS of proposed conductor. | Tension at 0°C and 2/3 wind condition (32 kg/m2 wind pressure); ≤ 4523 kg & not exceeding 70% of UTS of proposed conductor. |