| # Sl. No. | # Volume/ Section/ Description | # Clauses | # Bidder’s Query | # POWERGRID Reply |
| --- | --- | --- | --- | --- |
| # Volume-II; Technical Specifications (Doc. Code No. DC-3071-15728, Nov 2020) |  |  |  |  |
|  | Clause 2.2.2.2 ( B) of Section Project | (B) Dismantling Works : a) Dismantling of equipment foundations. b) Dismantling, Transportation, loading and unloading of 400 kV BPI along with Support Structure , associated connectors, AL tubes & 145kV Isolators presently being used for NGR Bypass etc and handing over to stores of POWERGRID at Bina (PG) S/s. | The referred clause states that "Dismantling, Transportation, loading and unloading of 400 kV BPI along with Support Structure, associated connectors, AL tubes & 145kV Isolators presently being used for NGR Bypass etc and handing over to stores of POWERGRID at Bina (PG) S/s in scope of the Contractor. Kindly confirm that the Insurance required for the above scope of works shall be taken by PGCIL and not by the Contractor. | The Insurance required for this work shall be in Scope of Contractor. |
|  | Clause 2.1.5 | Supply, erection, testing and commissioning of 1 number of 500 MVA, 400/220/33kV Autotransformer each at Wardha, Seoni & Morena substations is covered under separate package. However associated civil works for these owner supplied materials is covered under present scope. | The said clause states that the supply of Auto Transformer is covered under separate package. Kindly confirm the delivery schedule of Auto Transformer at Site, in order to plan proper execution schedule and avoid any delays. | Bidder may Quote as per Schedule Completion Specified for this package. |
|  | Clause 1.3 of Section Project | 1.3 Associated Transmission System: The following transmission system is envisaged under WRSS-23: i) Augmentation of 1X 500 MVA, 400/220kV ICT (3rd) at 765/400/220kV Wardha 400/220kV Substation. ii) Augmentation of 1X 500 MVA, 400/220kV ICT (3rd) at 765/400/220kV Seoni 400/220kV Substation. iii) Augmentation of 1X 500 MVA, 400/220kV ICT (3rd) at Morena 400/220kV Substation of CWRTL. iv) Conversion of 50 MVAR Fixed Line reactor at Bina (PG) end of Sagar (MP)-Bina (PG) 400kV Line into switchable line reactor along with NGR by pass arrangement. | From the refered clause, we understand that existing Morena Substation is under CRWTL. (Part of Adani). In view of the above, kindly confirm the extent of involvement of Adani during execution stage. Also, please confirm that PGCIL shall be responsible to obtain necessary approvals and permission required in order to carry out the works at Morena S/S. | All engineering submission and approval shall be done by Employer. For Day to day activity at site needful coordination with M/s CRWTL shall be done by contractor. All needful support as per provision of contract shall be provided by Employer. |
|  |  |  | With reference to the above clause, please confirm that Handing over of Morena Substation shall be to PGCIL and not to Adani after succesfull completion of works. | After Completion of work bays under present scope shall be handed over to Employer. |
|  | Annex-I of Section project | List of Drawings | Transformer side Tension, Suspension Insulator, Jack bus is in Contractor's scope (as marked in Red) as shown in Section Layout of Wardha Substation, However, during site visit it's observed that above stated items already exist. Kindly confirm the requirement. | Bidder may quote as per provision indicated in Drawing ref C/ENGG-SS/WR/WR/WRSS-23/WARDHA/PLAN-SEC/01 |
|  | Schedule 1 of BPS |  | For Seoni ss : Number of SAS Augmentation for 400kV Main bay has been mentioned as 2 in the Price schedule (No: 22) , as per the SLD only one Main bay and one Tie bay has been shown ,kindly clarify. | Bidder may Quote as Per BPS |
|  | Schedule 1 of BPS |  | For Bina ss: , In Price schedule , one separate line item for supply of BCU has been mentioned (No: 5), hope this BCU will be mounted in the CB relay panel itself | Confirmed. |
|  | General |  | Hope there is no supply of numerical relay test kit applicable. | Bidder may Quote as per BPS |
|  | General |  | Please provide details of Existing HVWS Hydrant Layout /tapping details from existing system for respective substations as per scope of work, | Existing Fire protection layout shall be provided to successful bidder during detailed engineering state. However For nearest taping point for Fire protection System is specified in Section project |
|  | General |  | Please provide details of Existing Earthing drawing details at Morena substation | Existing layout of Morena S/s shall be provided to successful bidder during detailed engineering Stage |
|  | General |  | Please provide details for 415V ACDB & 220KV DCDB existing drawing at Morena Substation for extension scope | Existing ACDB & DCDB drawings at Morena S/s shall be provided to successful bidder during detailed engineering stage |
|  | General |  | Please provide Location details of Protection & Control panels for placing proposed panels at Wardha and Bina Substation and distance from proposed bays. | The Panels shall be located in Bay SPR of respective bays. Bidder May visit the site & get acquaint with existing facilities |
|  | General |  | We understand that CRP for both 400KV & 220KV at Seoni & Morena Substations shall be placed in proposed switchyard control room at 400KV Side. Kindly confirm | For Seoni S/s One number of New SPR is considered for locating HV Protection Panels of ICT. Protection Panels of LV Side shall be located in nearest existing Switchyard panel Room (SPR). For Morena : Two New SPR ( One for 400kV Switchyard & One for 220kV Switchyard is specified in BPS) |
|  | Schedule 3 of BPS |  | Extension of Wardha S/S : We understand that bidder’s to modify existing 315mvaR Transformer foundation as per tender drawing C/ENGG/MOD/TRF/FDN/WADHA/11 to suit 500mvaR Transformer (Areva Make). Please confirm. Also, please share foundation detailed drawing. | The Existing Foundation Drawing of ICT Foundation shall be provided to successful bidder during detailed engineering stage. |
|  | Annex-I of Section Project |  | Plan and Section Drawing for 400/220kV Morena Substation Ext.:- We understand that available 400kV Gantries at site are designed for additional beam load (arrangement as per layout) and bidder’s to follow PGCIL standard gantries as marked in Layout. Kindly confirm | Bidder may Quote as per Provision Shown in Drawing ref C/ENGG/WR/WRSS-23/MORENA/ GA/01 |