## Pre Bid Queries
CLARIFICATION-I dtd. 23.09.2020 FOR SUPPLY, INSTALLATION & COMMISSIONING OF AUTOMATIC FIRE SUPPRESSION SYSTEM AT 10 NOS. TELECOM LOCATIONS UNDER ERTCC, SPECIFICATION NO.: ERTCC/CS/20-21/I-236/T-175/AFSS(RFx: 5002001381)
Sr. No. | Bidding Document |  | Subject | Bidder’s Queries | POWERGRID reply | Clause to be amended
| Page No. | Clause No.
1 | Pg.21 of 22 | Sec. III BDS Volume.-I (BID DATA SHEETS (BDS)) ITB 24.1 © | Work Completion Schedule is 6 months from the date of Notification of Award | The pandemic caused by coronovirus(COVID-19) is having increasing impact in India & Globally also. Due to covid19 situation, It's difficult to supply, installed & commissioning of AFSS within 6 months thus we request you, Kindly accept completion period 8 months from the date of notification of award. | In view of global pandemic caused by Corona virus (COVID-19), the extension of delivery schedule may be accepted | Refer Amendment-I
2 |  | Technical Experience | The Bidder must have supplied, installed, tested and commissioned Automatic Fire suppression/Fire Fighting system at Two (2) Telecom Establishment/Data center/any commercial installation in India, within last seven (7) years and which must have been in satisfactory operation# for at least one (1) year as on the originally scheduled date of bid opening | We have recently participated in PGCIL Tender No.NRTCC/CS/20-21/Fire Alarm/1190. There has been mentioned following technical experience. "The Bidder must have supplied, installed, tested and commissioned Automatic Fire suppression/Fire Fighting system at One Telecom Establishment/Data center/any commercial installation in India, within last seven (7) years and which must have been in satisfactory operation# for at least one (1) year as on the originally scheduled date of bid opening'' We request you, Kindly accept same for this tender. | QR condition shall prevail | No change
3 | Pg.2 of 16 | Technical specification | The system shall be designed with minium design concentration of 4.7% as applicable of class A & C fires. | As per NFPA 2001 latest edition on 2018, Novec1230 design concentration is 4.5% for Class A & C fires. Kindly accept same. | As per NFPA-2001 latest edition on 2018 design concentration, the AFSS system with minimum design concentration of 4.5%(earlier 4.7%) as applicable to class A7C fire for NOVEC 1230 may be accepted. | Refer amendment-I
4 | Pg 6 of 16 | Technical specification | Wiring shall be installed in electrical mettalic tubing(EMT) or MS/GI conduit. | Control cable 2Cx1.5mm2 FRLS PVC armoured cu. Conductor is mentioned in BOQ of price bid format. Kindly clarify, What will be Bidder follow technical specification or Price bid format of PGCIL? | TS and BoQ both conditions shall prevail | No change
5 |  |  | General | We request you, Kindly provide us GA drawing or details of room dimensions(LengthxWidthx Height which is inclusive of Ceiling void, Room Void, Floor Void) for each locations. | Detail attached as annexure-I | No change
6 |  |  | General | As per BOQ, M/s. PGCIL has requirement of addressable fire alarm cum gas release panel for more than 4 zones, 4 Zone & 2 Zone fire alarm cum gas release panel instead of these Bidder will provide gas release panel i.e. suitable for all protected area. Kindly confirm this is accpetable. | TS condition shall prevail | No change
7 |  |  | General | We understand, M/s. PGCIL has provided specification of only gas release panel And not addresaable Fire Alram cum gas release panel. Plz, Confirm the exact requirement. | The contactor may offer UL listed /FM or Vds approved addresaable Fire Alram cum gas release panel and which meets TS and BOQ requirement | No change
8 |  |  | General | We understand from price bid format of PGCIL, There are 14 Nos. of rooms are protected through gas suppression system. Kindly clarify? | presently 14 rooms are to be equipped with AFSS spread over 10 location. However during detailed engineering / survey if 2 or more rooms are merged into one or technically it is found that single unit will serve the purpose , only one unit shall be considered for billing purpose for line item D(sch-2),A(sch-3) &B(sch-4(b)) | No change
9 |  |  | General | PGCIL has mentioned in price bid format, AMC charges during warranty period is 10 Nos(Qty.) & AMC charges after warranty period is 14 Nos(Qty.). We request you, Kindly recheck & confirm all quantity of price bid format. | Item under price schedule for AMC charges during warranty period deleted | Refer Amendment-I
10 | 6 | 3.Section-III_BDS Vol.I | Class -1 Local Content, Firms who are not ‘Class-I local supplier’ shall not be eligible to bid. The ‘Class-I local supplier’ shall give a self-certification in his bid in the given format, indicating the percentage of Local Content and certifying that the item offered meets the Local Content requirement for ‘Class –I local supplier’ and shall give details of the location(s) at which value addition is made. | With reference to the technical specification(Page No. 1), Automatic Fire Suppression System should be UL Listed & FM Approved system, which is normally imported and as per tender term we need to comply "Class-I Local Supplier" | Tender condition (BDS)shall prevail. | No change
Please confirm.
11 | 1 of 1 | BoQ | Type of tender | This refers to the Tender BOQ, as we understood the offer price is as per BOQ based. In case of quantity increase during detail engineering the same will amend in PO as per pro rata basis. Hence, if any extra special item is required to commission the system that should be provided by the bidder without any extra cost implication. Please confirm. | Dimension of room is provided in the Bid as Annexure-I. Hence , if any extra special item is required to commission the system that shall be in scope of the contractor without any extra financial implication to POWERGRID. | No change
12 | 12 of 15 | SECTION – III; BDS(ITB 13.1) | BID SECURITY / EARNEST MONEY DEPOSIT (EMD) | As a MSME vendor we request to wave off our EMD amount & exception to submit the EMD. We have also enclosed our MSME certificate for your confirmation. | Provision already maintained in bidding document | No change
13 | 1 of 16 | Technical Specification(2) | Design Condition "The software calculation shall be VdS or FM/UL approved". | Your technical specifications are contradictory with each other. If a vendor goes with a VdS approved gas suppression system then he has to consider other mechanical line items also for same approvals like Nozzles, Hose, Valves, Actuator, Low pressure switch etc. Please allow & confirm. |  | No change
| 1 of 16 | Technical Specification(1) | Introduction "Only UL listed or FM approved control Panel, abort switch, Electrical Actuator, low pressure switch, manual actuator, valves, hose, nozzles, hooter & Strobe and other electrical system shall be offered". |  |  | Refer Amendment-I
| 5 of 16 | Technical Specification(4.4) | Detection Arrangment "Smoke Detectors shall confirm to IS-11360-1985 or BS-5446 Part I-1977 & Part VII-1985 (VdS/LPCB approved) or NFPA72 (UL/ULC/FM approved) amended upto date". |  |  | No change
14 | 4 of 16 | Technical Specification(4.3.1) | Discharge Nozzle "Noise level of nozzle shall be less than 100dB." | Noise level gives impact only in the data center, where data storage hard disk is giving problems for more than 120dB noise level. Our offered system nozzle noise level is below 120dB from 1mtr distance, which does not give any technical effect for other installed equipment. Please find enclosed test certificates & allow for the same. | TS condition shall prevail | No change
15 | 10 of 16 | Technical Specification(10.0; Sub Clause b) | Warranty & Annual Maintenance Contract | Refer to your Warranty & Annual Maintenance Contract clause as we understood, bidder not need to depute dedicated manpower 24x7 days basis, bidder will provide manpower yearly two times only for preventive comprehensive maintanance & unlimited breakdown call in case of emergency only. Please confirm. | The contrator need to maintain TAT | No change
16 | N/A | General | Room Details | Refer to your BOQ sheet, only cylinder nos is mentioned. We wish to inform you cylinder size will be differ from 22 lit to 140 lit based on room design calculation. Based on that hige cost implecation is there. You are requested to room size detais (width, breadth & height) with details of False ciling and false floor (if there). Its help us to better clarification & good service support during execution of project & govt. also can enjoy the price benifit. | Room size details attached as Annexure-I | Annexure-I added in Bidding Document Vol-II
17 | NA | NA | work duration | The tender confirms that the contract durations is 12 months from NOA. However, it also mentions that the scope work completion schedule is 6 months from NOA. We request you to clarify this statement. | For awarded work completion time will be 8 month and if any site added then duration may extend to 12 month. | Refer Amendment-I
18 | NA | NA | EMD | Please confirm that tender fee and EMD are exempted for SME companies | Please refer to BID document | No change
19 | NA | NA | Payment terms | Please confirm the payment terms of the contract | Please refer to BID document | No change
20 | NA | Technical Specification | Proto/ type testing | Please also confirm that the discharge of agent will be carried out at only the smallest of the sites during Proto Testing/ Type Testing. No other discharge test during either FAT or SAT shall be carried | The discharge of agent will be carried out at only the smallest of the sites during Proto Testing​. | No change
21 | 5 | Technical Specification(4.5) | Gas release panel | Technical Specifications, Clause No. 4.5, Page No. 5: Tender calls for a conventional gas release panel. However, conventional gas release cannot be connected to a computer to download the panel data. Hence, we request you to waive this clause. | The data from the control panel can be downloaded to laptop/PC at later stage on requirement basis. | No change
22 | 6 | Technical Specification(5) | Installation & commissioning | 1. Technical Specifications, Clause No. 5, Page No. 6: Please confirm that the installation can be carried out an agency that is certified by the OEM of the Clean Agent System. | The installation of the entire system has to be done by agency certified by National/International agency/laboratory | No change