| S. No. | Volume/Section Clause No. |  | Description | Clarification requested | POWERGRID’s Clarification |
| --- | --- | --- | --- | --- | --- |
|  | Vol-II - Section - Projects; Cl. 2.1 Name of Substation: Extn. of 765/400KV Jhatikara Sub-Station; sub clause A-I; page 5 of 38 |  | Dismantling, Shifting and re-erection, testing and commissioning of 3X80MVAr, 765kV Bus Reactors of M/s TBEA make (main units) along with associated equipment from Bay no. 706 to Bay no. 701 including neutral Formation & Spare Reactor connection arrangement for above Reactors | Section projects & Single line diagram calls for dismantling of 3x80MVAR reactors from bay No. 706 to bay No. 701. Whereas the General Arrangement Drawing shown with Spare reactor on bay No. 701 and extension of Common 765kV auxiliary bus and Neutral bus extension upto bus reactor bay-II (Bus reactor-II shown as is future). | 3x80MVAR reactors are to be shifted from bay No. 706 to bay No. 701. Bidder to quote as per the scope mentioned in Section Project. |
|  | Vol-II - Drg. No. C/ENGG-SS/NR-I/RTM/JHATIKRA/SLD/01; 765/400kV Single Line Diagram |  |  | As per the existing arrangement in bay 706 is 4x80MVAR inclduing spare is there. Converting the Bay 706 as Transformer feeder the existing spare reactor also has to be shifted to bay number 701 as shown in General arrangement drawing for space requirement. Kindly clarify | Refer our reply above at S.no.1. |
|  | Vol-II - Drg. No. C/ENGG-SS/NR-I/RTM/JHATIKRA/GA/01 (SHEET 1 OF 2) General Arrangement drawing |  |  | Over and above, over head line is shown for common neutral bus extension from bay Number 701 to Bus reactor-II units. For 765kV spare common bus, rigid bus arrangement with BPI support is shown in the General arrangement drawing. Kindly confirm our above understanding. | 145 kV Aux Bus is envisaged through over-head line and 765 kV Aux Bus is envisaged through IPS tube. |
|  | Vol-II - Technical specification for 400kV & 220kV GIS (GIS-REV 5A) Vol-II - Technical specification for 400kV & 220kV GIS (GIS-REV 5A) Vol-II - Technical specification for 400kV & 220kV GIS (GIS-REV 5A) Vol-II - Technical specification for 400kV & 220kV GIS (GIS-REV 5A) Vol-II - Technical specification for 400kV & 220kV GIS (GIS-REV 5A) Vol-II - Technical specification for 400kV & 220kV GIS (GIS-REV 5A) | 2.3 | The equipment offered shall be protected against all types of voltage surges and any equipment necessary to satisfy this requirement shall deemed to be included. | We understand that surge arrestors are required to cater the requirement and are of AIS type. | Bidders understanding is correct. |
|  |  | 5.8. | The material and thickness of the enclosures shall be such as to withstand an internal flash over without burns through for a period of 300 ms at rated short time withstand current. The material shall be such that it has no effect of environment as well as from the by-products of SF6 breakdown under arcing condition. This shall be validated with Type Test. | The Value shall be in line with the requirement of IEC 62271-203. Request a concurrence on the same. | Bidder to quote as per the provision in TS. |
|  |  | 5.9 | Inspection windows (View Ports) shall be provided for Disconnect Switch and both type of earth switches i.e. Maintenance and fast operating. | Inspection windows shall be provided for Disconnector enclosures. Provision of Observation windows for Earth switches is not envisaged as such. | Bidder to quote as per the provision in TS |
|  |  | 5.21. | The GIS shall be designed, so as to take care of the VFT over voltages generated as a result of pre-strikes and re-strikes during isolator operation. Maximum VFT over voltages peak shall not be higher than rated lightning impulse withstand voltage (LIWV) of the equipment. Necessary measures shall be under taken by GIS manufacture to restrict maximum VFT over voltages lower than the LIWV. Manufacturer shall submit the study report of VFTO generated for GIS installation. | For an 220 kV GIS system, we do not envisage VFTO studies. Hence, the same shall be excluded from GIS OEM scope of supply. | Bidder to quote as per the provision in TS |
|  |  | 5.25 | The switchgear shall have provision for connection with ground mat risers through copper connections. This provision shall consist of grounding pads to be connected to the ground mat riser in the vicinity of the equipment. | Earthing details shall be provided during detailed engineering stage. However, supply of earthing materials shall be excluded from GIS OEM GIS Ltd. scope of supply. | Bidder to quote as per the provision in TS. |
|  |  | 5.31 | ii) Any other alarm necessary to indicate deterioration of the gas insulating system. | Not Applicable for the offered GIS | Bidder to quote as per the provision in TS. |
|  |  | 5.41. | Gas Insulated Bus (GIB) layout: The horizontal clearance between GIB and GIS building /any other building wall shall be preferably three (3) meters. | The space/area utilization for such a configuration is very high and request customer to accept the standard spacing's between circuits considering the fact that the Bus-ducts are passive and requires almost no maintenance. Request PGCIL to accept the same. | Bidder to quote as per the provision in TS. |
|  |  | 6.6.8. | Circuit Breaker shall be supplied with auxiliary switch having additional 8 NO( normally open) and 8 NC ( normally closed) contacts for future use over and above those required for switchgear interlocking and other control and protection function. These spare NO and NC contacts shall be wired upto the local control cubicle. | Auxiliary switches are of standard design/size suitably designed for the available space. Hence the required additional 8 NO (Normally open) and 8 NC (normally closed) contacts shall be provided to customer through contact multiplication relays at LCC. | Bidder to quote as per the provision in TS. |
|  |  | 6.7.2. | Control: The breaker shall normally be operated by remote electrical control. Electrical tripping shall be performed by shunt trip coils. However, provisions shall be made for local electrical control. For this purpose a local/remote selector switch and close and trip control switch/push buttons shall be provided in the breaker control cabinet. | As per our standard practice the Local/Remote switches will be provided in the Local Control Cubicle (LCC). | Bidder to quote as per the provision in TS. Local/Remote switches provided in the Local Control Cubicle (LCC) accepted, meeting Functional requirement as per TS. |
|  |  | 7.2.5 | For motor-operated disconnect switches, the control should be electrically and/or mechanically uncoupled from the drive shaft when the switch is operated manually to prevent coincident power operation of the switch and the drive mechanism(s). | Only electrical inter-locks possible between DS & ES. We do not envisage providing any mechanical interlocks. Request customer to kindly accept the same. | Bidder to quote as per the provision in TS. |
|  |  | 7.2.10 | Each disconnector shall be supplied with auxiliary switch having additional 8 NO (NormallyOpen) and 8 NC (Normally Closed) contacts for future use over and above those requiredfor switchgear interlocking and automation purposes. These spare NO and NC contacts shall be wired up to the local control cabinet. | Auxiliary switches are of standard design/size suitably designed for the available space. Hence the required additional 8 NO (Normally open) and 8 NC (normally closed) contacts shall be provided to customer through contact multiplication relays at LCC. | Additional Auxiliary switches as per TS in LCC panel meeting functional requirement of TS are acceptable. |
|  |  | 7.2.13 | The disconnectors and safety grounding switches shall have a mechanical and electrical inter-locks to prevent closing of the grounding switches when isolator switches are in the closed position and to prevent closing of the disconnectors when the grounding switch is in the closed position. Integrally mounted lock when provided shall be equipped with a unique key for such three phase group. Master key is not permitted. | The disconnectors and the safety grounding switches are separate modules in GIS design and shall have only electrical inter-locks between them. However the required padlocking facility shall be provided for the manual interlocking for additional protection. | Bidder to quote as per the provision in TS. |
|  |  | 8.2 | Each safety grounding switch shall be electrically interlocked with its associated disconnectors and circuit breaker such that it can only be closed if both the circuit breaker and disconnectors are in open position. Safety grounding switch shall also be mechanically key interlocked with its associated disconnectors. | The disconnectors and the safety grounding switches are separate modules in GIS design and shall have only electrical inter-locks between them. However the required padlocking facility shall be provided for the manual interlocking for additional protection. | Bidder to quote as per the provision in TS. |
|  |  | 8.6 | Each ground switch shall be fitted with auxiliary switches having 4 NO (Normally Open) and 4 NC (Normally Closed) contacts for use by others over and above those required for local interlocking and position indication purposes. | Auxiliary switches are of standard design/size suitably designed for the available space. Hence the required additional 4 NO (Normally open) and 4 NC (normally closed) contacts shall be provided to customer through contact multiplication relays at LCC. | Refer our reply to the similar query above |
|  |  | 9.9 | Each high speed ground switch shall be fitted with auxiliary switches having 4 NO (Normally Open) and 4 NC (Normally Closed) contacts for use by others, over and above these required for local interlocking and position indication. | Auxiliary switches are of standard design/size suitably designed for the available space. Hence the required additional 4 NO (Normally open) and 4 NC (normally closed) contacts shall be provided to customer through contact multiplication relays at LCC. | Refer our reply to the similar query above |
|  |  | 11.3.2 | Surge arrestor shall be disconnect-link type and be attached to the gas-insulated system in such a manner that they can be readily disconnected from the system while the system is being dielectrically tested. | Noted. However gas works shall be required to do the same. Also we do not foresee any requirement of GIS LA. | Bidder to quote as per the provision in TS. |
|  |  | 15.2.1 | It shall comprise structural frames completely enclosed with specially selected smooth finished, cold rolled sheet steel of thickness not less than 3 mm for weight bearing members of the panels such as base frame, front sheet and door frames, and 2.0mm for sides, door, top and bottom portions. | As per the standard pratice, for the weight bearing members a sheet thickness of 2.5 mm is more than sufficient and as a GIS manufacturer we recommeded the same and for non weight bearing members the same is 2 mm thick. We request customer to kindly confirm the same. | Bidder to quote as per the provision in TS. |
|  |  | 22 | All transport packages containing critical units viz Circuit breakers and Voltage transformers shall be provided with sufficient number of impact recorders (on returnable basis) during transportation to measure the magnitude and duration of the impact in all three directions. | VTs being an critical equipment only impact recorders shall be provided for VTs. We request customer to kindly accept the same. Also we do not foresee any requirement of GIS VT. | Bidder to quote as per the provision in TS. |
|  | Vol-II - Technical specification | Annexure A, Sheet 2 of 2 |  | Our type tested 245KV GIS has passive busbar design. We meet the requirement of service continuity, maintenance & repair without provision of any barrier in busbar. All the requirement of repair & maintenance as per specifications are met with passive non-segregated busbar design. This design is accepted by various utilities in India and Abroad. This type of passive non-segregated busbar design is working satisfactorily at site without any issues hence we request an acceptance of this design. | Bidder to quote as per the provision in TS. |
|  |  | Annexure A, Sheet 1 of 2 |  | Our type tested 400KV GIS has passive busbar design. We meet the requirement of service continuity, maintenance & repair without provision of any barrier in busbar. All the requirement of repair & maintenance as per specifications are met with passive non-segregated busbar design. This design is accepted by various utilities in India and Abroad. This type of passive non-segregated busbar design is working satisfactorily at site without any issues hence we request an acceptance of this design. | Bidder to quote as per the provision in TS. |
|  |  | KPS-2 400kV GIS Busduct Extension | Pressure difference between existing and present scope GIS. | There is a difference in rated SF6 filling pressure across different OEMs. Hence to integrate existing GIB with new OEM GIB, requesting PGCIL to allow to fill SF6 gas inside extension adaptor at a pressure nearly matching existing GIB rated pressure | Bidder to quote as per the provision in TS. |
|  |  |  | Floor level at KPS-2 S/s | We require section view of the switchyard to assess floor level. We are assuming flat surface without any elevation/decline. Kindly confirm. | There is no level difference on 400 kV Switchyard for GIB route. |
|  |  |  | Online PD monitoring / online Gas monitoring | We assume no online PD monitoring/ Gas monitoring is required. Kindly confirm. | Confirmed. |
|  | Section Project | 2.3 | 400kV: 400kV line is to be connected in existing 400kV Line Bay Module provided with interface module brought out of GIS Hall in existing diameter comprising of LWSR(F)-Tie-Line. | We understand Interface module brought out of GIS Hall in existing diameter have isolating link and terminated with Gas tight bushing by existing supplier. We also require drawing and gas pressure details of exisiting GIB to check our adaptor compatibility. | Interface Module drawing of existing GIS shall be shared during detailed engineering. |
|  | KPS-2 |  | GIB to GIB extension adaptor | Extension adaptor not mentioned in BOQ as separate line item. Kindly include the same. | Bidder to quote as per the provision in TS and BPS. |
|  | KPS-2 400kV GIS Busduct Extension |  | General Scope | The technical details of the Existing GIS, its end flange and other details required. | Refer our reply to the similar query above. |
|  |  |  |  | It is requested to share existing LCC drawings and space availability in GIS hall to check feasibility of interconnection. Necessary cable for gas density monitors shall be provided however supply of LCC inter connection with existing LCC sha | Existing LCC drawings and other details shall be shared during detailed engineering with successful bidder. |
|  |  |  |  | We assume PGCIL shall support with necessary spares available at site. If required during installation of Bus duct with existing GIS. | Bidder to quote as per the provision in TS. |
|  |  |  | Activity Description; Item Description; Unit; Qty.. I; Extn of 400kV KPS-02 SS. GIS Portion 420 kV Equipment; 420kV, 3000A, 63kA, Single phase, SF6 Gas Insulated Bus Duct (GIB) outsideGIS Hall alongwith associated supportstructure; M; 1,000.00. GIS Portion 420 kV Equipment; 420KV, 3150A, 63KA SF6 TO AIR BUSHING including support structure; SET; 3.00. | Bidder understand that the Supply/Integration of the Online /Offline PD Monitoring System not in the Bidder Scope. Kindly confirm. | Supply Online /Offline PD Monitoring System not envisaged. |
|  |  |  | Activity Description; Item Description; Unit; Qty.. I; Extn of 400kV KPS-02 SS. Mandatory Spares-AIS; Relay & protection Panels (with automation); LS; 1.00. Mandatory Spares-AIS; Spares-Substation Automation System; LS; 1.00. Mandatory Spares-AIS; SPARES FOR CLAMPS & CONNECTORS; LOT; 1.00. Mandatory Spares-AIS; Spare-420kV BPI; SET; 1.00. | Detailed Qty is not available in the Mandatory Spares List. Kindly Provide the Qty. | Refer Annexure-III Section Project |
|  |  |  | Activity Description; Item Description; Unit; Qty.. III; SS EXTN FOR 1x500 MVA ICT at Rajgarh. 220 kV GIS EQUIPMENT; 245kV, 1600A, 50kA Single phase SF6 to Air Bushing; EA; 3.00. 220 kV GIS EQUIPMENT; 245KV,1600A, 50KA, SINGLE PHASE, SF6 GAS INSULATED BUS DUCT (GIB)OUTSIDE GIS HALL ALONGWITH ASSOCIATED SUPPORT STRUCTURE ETC. AS PER TECHNICAL SPECIFICATION; M; 300.00. 220 kV GIS EQUIPMENT; 245 kV, 3000A, 50kA, SF6 GIS Bus barmodule as per Section-Project,Technical specification; SET; 2.00. 220 kV GIS EQUIPMENT; 245kV, 1600 A, 50 kA, SF6 GIS ICT feederbay module as per Section-Project,Technical specification; SET; 1.00. | Bidder understand that the Supply/Integration of the Online /Offline PD Monitoring System not in the Bidder Scope. Kindly confirm. | Refer our reply to the similar query above. |
|  |  |  | Activity Description; Item Description; Unit; Qty.. IV; 220kV GIS line bay at 400/220kV Rajgarh. 220 KV GIS Equipments; 245kV, 1600 A, 50 kA, SF6 GIS Linefeeder bay module as perSection-Project, Technicalspecification; SET; 1.00. 220 KV GIS Equipments; 245kV, 1600A, 50kA Single phase SF6 to Air Bushing; EA; 3.00. 220 KV GIS Equipments; 245KV,1600A, 50KA, SINGLE PHASE, SF6 GAS INSULATED BUS DUCT (GIB) OUTSIDE GIS HALL ALONGWITH ASSOCIATED SUPPORT STRUCTURE ETC. AS PERTECHNICAL SPECIFICATION; M; 150.00. | Bidder undersand that the Supply/Integration of the Online /Offline PD Monitoring System not in the Bidder Scope. Kindly confirm. | Refer our reply to the similar query above. |
|  |  |  | Activity Description; Item Description; Unit; Qty.. IV; 220kV GIS line bay at 400/220kV Rajgarh. Mandatory spares-220kV (lot); Spare-PLCC; SET; 1.00. | PLCC Items are not available in in the Main BOQ. Make & Detailed of Scope of works is not available in the Section Projects. Kindly provide the Make details if the Spares are required for Existing PLCC Equipments. | Bidder to quote as per the provision in Bidding Documents. |
|  |  |  | Activity Description; Item Description; Unit; Qty.. V; 400/220kV Pavagda extn. 220kV EHV Cable & Associated Equipments; 220 KV OUTDOOR TERMINATION KIT SUITABLE FOR 220 KV XLPECABLE; SET; 8.00. 220kV EHV Cable & Associated Equipments; 220KV HV POWER CABLE ALONG WITH ACCESSORIES; KM; 2.00. | Bidder undersand that the DTS systems not required for the 220kV Cable System. Kindly confirm. | As per clause 2.4-A-IV of Section Project DTS for 220 kV EHV cable is not envisaged. |
|  | -- |  | -- | Extension module details and drawing to prepare extension adaptor for KPS-2 | The Existing details shall be shared during detailed engineering in case of award. |
|  | -- |  | -- | Rated, burst and minimum pressure of existing GIB for KPS-2. | The Existing details shall be shared during detailed engineering in case of award. |
|  | -- |  | -- | O-ring and other components/parts of existing GIS are to be supplied by PGCIL or PGCIL shall arrange from existing vendor. (for KPS-2) | POWERGRID do not envisaged any GIS Owner Supplied Material for successful completion of scope under present scope. |
|  | -- |  | -- | Section profile of switchyard of KPS-2 | The Existing details shall be shared during detailed engineering in case of award. |
|  | -- |  | -- | Extension adaptor to be mentioned in BOQ as separate line item. | Bidder to quote as per the provision in Bidding Document. |
|  | -- |  | -- | We assume the termination of present scope GIB gas density monitor signals; existing GIS LCC shall be utilized. Hence request PGCIL to arrange supervisor from existing GIS supplier-Kindly Confirm | Supervisor from existing GIS supplier, if necessary, may be arranged by contractor. |
|  | -- |  | -- | We assume no online PD monitoring/ Gas monitoring is required. Kindly confirm. | Online PD monitoring System is not envisaged under present scope. |
|  | -- |  | -- | Sufficient space without any obstruction in switchyard for free movement of installation and testing equipment /hydra/crane - Kindly confirm | POWERGRID shall provide owner supplied facilities as per the provision in Bidding Documents. |
|  | Price_schedule_SS-129 |  | IV 220kV GIS line bay at 400/220kV Rajgarh (item no. 30) Spare-PLCC - 1 Set | Annexure-III Manadatory Spare Breakup does not contain break up of PLCC Spares. Please provide list of same. | Refer Annexure-III Section Project of Technical Specification. |
|  | 1.0 Section Project_R0 & 21.0 EHV XLPE cable Rev01 |  | Section Project Clause No. XIV 220kV, EHV XLPE cable & Clause No. 1.2 of SECTION: EHV XLPE POWER CABLE | AS per Section project it is mentioned that, The conductor and size of cable shall be copper and 2500Sq.mm. respectively. However as per 21.0 EHV XLPE cable Rev01 of Vol-II Part 13 it is mentioned that The EHV grade cable shall be single core, unarmoured, stranded, compacted/Segmental Aluminium/Copper (as specified in BPS) The BPS does not mention any detail of cable size or type. Hence please confirm the conductor of 220kV cable is Alumium or Copper | Bidder to quote as per the requirement specified in Section Project. Also, may please refer the order of precedence for Model Section of TS and Section Project. |
|  | 1.0 Section Project_R0 & 21.0 EHV XLPE cable Rev01 |  | Section Project Clause No. XIV 220kV, EHV XLPE cable & Clause No. 1.2 of SECTION: EHV XLPE POWER CABLE | As per 21.0 EHV XLPE cable Rev01 of Vol-II Part 13, it is mentioned that "The EHV grade cable shall be single core, unarmoured, stranded, compacted/ Segmental Aluminium/Copper (as specified in BPS) conductor, core screening by a layer of semiconducting tape followed by a layer of semiconducting compound, cross linked polyethylene (XLPE) dry cured insulation, insulation screening with semiconducting compound extruded directly over the insulation, longitudinal sealing by a layer of non woven tape with water swellable absorbent over insulation screen, followed by radial sealing (Metal sheath of Lead alloy ‘E’ / Corrugated Aluminium, (unless otherwise specified in Section Project)" However in Section project nothing is mentioned regarding corrugation of Cable. Hence please confirm the corrugation of 220kV Cable, whether it is Metal sheath of Lead alloy or Aluminium | Conductor and size of cable shall be copper and 2500Sq.mm as specified in Section Project. For the further detail, Model TS section EHV XLPE cable Rev01 shall be referred to. |