| S. No. | Volume/Section Clause No. | Description | Clarification requested | POWERGRID’s Clarification |
| --- | --- | --- | --- | --- |
| Technical specification for 400kV & 220kV GIS (GIS-REV 5A) |  |  |  |  |
| 1 | 2.3 | The equipment offered shall be protected against all types of voltage surges and any equipment necessary to satisfy this requirement shall deemed to be included. | We understand that surge arrestors are required to cater the requirement and are of AIS type. | Refer our reply already given to the similar queries in Clarification-I. |
| 2 | 5.8. | The material and thickness of the enclosures shall be such as to withstand an internal flash over without burns through for a period of 300 ms at rated short time withstand current. The material shall be such that it has no effect of environment as well as from the by-products of SF6 breakdown under arcing condition. This shall be validated with Type Test. | The Value shall be in line with the requirement of IEC 62271-203. Request a concurrence on the same. | Refer our reply already given to the similar queries in Clarification-I. |
| 3 | 5.9 | Inspection windows (View Ports) shall be provided for Disconnect Switch and both type of earth switches i.e. Maintenance and fast operating. | Inspection windows shall be provided for Disconnector enclosures . Provision of Observation windows for Earth switches is not envisaged as such. | Refer our reply already given to the similar queries in Clarification-I. |
| 4 | 5.21. | The GIS shall be designed, so as to take care of the VFT over voltages generated as a result of pre-strikes and re-strikes during isolator operation. Maximum VFT over voltages peak shall not be higher than rated lightning impulse withstand voltage (LIWV) of the equipment. Necessary measures shall be under taken by GIS manufacture to restrict maximum VFT over voltages lower than the LIWV. Manufacturer shall submit the study report of VFTO generated for GIS installation. | For an 220 kV GIS system, we do not envisage VFTO studies. Hence, the same shall be excluded from GIS OEM scope of supply. | Refer our reply already given to the similar queries in Clarification-I. |
| 5 | 5.25 | The switchgear shall have provision for connection with ground mat risers through copper connections. This provision shall consist of grounding pads to be connected to the ground mat riser in the vicinity of the equipment. | Earthing details shall be provided during detailed engineering stage. However, supply of earthing materials shall be excluded from GIS OEM GIS Ltd. scope of supply. | Refer our reply already given to the similar queries in Clarification-I. |
| 6 | 5.31 | ii) Any other alarm necessary to indicate deterioration of the gas insulating system. | Not Applicable for the offered GIS | Refer our reply already given to the similar queries in Clarification-I. |
| 7 | 5.41. | Gas Insulated Bus (GIB) layout : The horizontal clearance between GIB and GIS building /any other building wall shall be preferably three (3) meters. | The space/area utilization for such a configuration is very high and request customer to accept the standard spacing's between circuits considering the fact that the Bus-ducts are passive and requires almost no maintenance. Request PGCIL to accept the same. | Refer our reply already given to the similar queries in Clarification-I. |
| 8 | 6.6.8. | Circuit Breaker shall be supplied with auxiliary switch having additional 8 NO( normally open) and 8 NC ( normally closed) contacts for future use over and above those required for switchgear interlocking and other control and protection function. These spare NO and NC contacts shall be wired upto the local control cubicle. | Auxiliary switches are of standard design/size suitably designed for the available space. Hence the required additional 8 NO (Normally open) and 8 NC (normally closed) contacts shall be provided to customer through contact multiplication relays at LCC. | Refer our reply already given to the similar queries in Clarification-I. |
| 9 | 6.7.2. | Control: The breaker shall normally be operated by remote electrical control. Electrical tripping shall be performed by shunt trip coils. However, provisions shall be made for local electrical control. For this purpose a local/remote selector switch and close and trip control switch/push buttons shall be provided in the breaker control cabinet. | As per our standard practice the Local/Remote switches will be provided in the Local Control Cubicle (LCC). | Refer our reply already given to the similar queries in Clarification-I. |
| 10 | 7.2.5 | For motor-operated disconnect switches, the control should be electrically and/or mechanically uncoupled from the drive shaft when the switch is operated manually to prevent coincident power operation of the switch and the drive mechanism(s). | Only electrical inter-locks possible between DS & ES. We do not envisage providing any mechanical interlocks. Request customer to kindly accept the same. | Refer our reply already given to the similar queries in Clarification-I. |
| 11 | 7.2.10 | Each disconnector shall be supplied with auxiliary switch having additional 8 NO (NormallyOpen) and 8 NC (Normally Closed) contacts for future use over and above those requiredfor switchgear interlocking and automation purposes. These spare NO and NC contacts shall be wired up to the local control cabinet. | Auxiliary switches are of standard design/size suitably designed for the available space. Hence the required additional 8 NO (Normally open) and 8 NC (normally closed) contacts shall be provided to customer through contact multiplication relays at LCC. | Refer our reply already given to the similar queries in Clarification-I. |
| 12 | 7.2.13 | The disconnectors and safety grounding switches shall have a mechanical and electrical inter-locks to prevent closing of the grounding switches when isolator switches are in the closed position and to prevent closing of the disconnectors when the grounding switch is in the closed position. Integrally mounted lock when provided shall be equipped with a unique key for such three phase group. Master key is not permitted. | The disconnectors and the safety grounding switches are separate modules in GIS design and shall have only electrical inter-locks between them. However the required padlocking facility shall be provided for the manual interlocking for additional protection. | Refer our reply already given to the similar queries in Clarification-I. |
| 13 | 8.2 | Each safety grounding switch shall be electrically interlocked with its associated disconnectors and circuit breaker such that it can only be closed if both the circuit breaker and disconnectors are in open position. Safety grounding switch shall also be mechanically key interlocked with its associated disconnectors. | The disconnectors and the safety grounding switches are separate modules in GIS design and shall have only electrical inter-locks between them. However the required padlocking facility shall be provided for the manual interlocking for additional protection. | Refer our reply already given to the similar queries in Clarification-I. |
| 14 | 8.6 | Each ground switch shall be fitted with auxiliary switches having 4 NO (Normally Open) and 4 NC (Normally Closed) contacts for use by others over and above those required for local interlocking and position indication purposes. | Auxiliary switches are of standard design/size suitably designed for the available space. Hence the required additional 4 NO (Normally open) and 4 NC (normally closed) contacts shall be provided to customer through contact multiplication relays at LCC. | Refer our reply already given to the similar queries in Clarification-I. |
| 15 | 9.9 | Each high speed ground switch shall be fitted with auxiliary switches having 4 NO (Normally Open) and 4 NC (Normally Closed) contacts for use by others, over and above these required for local interlocking and position indication. | Auxiliary switches are of standard design/size suitably designed for the available space. Hence the required additional 4 NO (Normally open) and 4 NC (normally closed) contacts shall be provided to customer through contact multiplication relays at LCC. | Refer our reply already given to the similar queries in Clarification-I. |
| 16 | 11.3.2 | Surge arrestor shall be disconnect-link type and be attached to the gas-insulated system in such a manner that they can be readily disconnected from the system while the system is being dielectrically tested. | Noted. However gas works shall be required to do the same. Also we do not foresee any requirement of GIS LA. | Refer our reply already given to the similar queries in Clarification-I. |
| 17 | 15.2.1 | It shall comprise structural frames completely enclosed with specially selected smooth finished, cold rolled sheet steel of thickness not less than 3 mm for weight bearing members of the panels such as base frame, front sheet and door frames, and 2.0mm for sides, door, top and bottom portions. | As per the standard pratice, for the weight bearing members a sheet thickness of 2.5 mm is more than sufficient and as a GIS manufacturer we recommeded the same and for non weight bearing members the same is 2 mm thick. We request customer to kindly confirm the same. | Refer our reply already given to the similar queries in Clarification-I. |
| 18 | 22 | All transport packages containing critical units viz Circuit breakers and Voltage transformers shall be provided with sufficient number of impact recorders (on returnable basis) during transportation to measure the magnitude and duration of the impact in all three directions. | VTs being an critical equipment only impact recorders shall be provided for VTs. We request customer to kindly accept the same. Also we do not foresee any requirement of GIS VT. | Refer our reply already given to the similar queries in Clarification-I. |
| 19 | Annexure A, Sheet 2 of 2 |  | Our type tested 245KV GIS has passive busbar design. We meet the requirement of service continuity, maintenance & repair without provision of any barrier in busbar. All the requirement of repair & maintenance as per specifications are met with passive non-segregated busbar design. This design is accepted by various utilities in India and Abroad. This type of passive non-segregated busbar design is working satisfactorily at site without any issues hence we request an acceptance of this design. | Refer our reply already given to the similar queries in Clarification-I. |
| 20 | Annexure A, Sheet 1 of 2 |  | Our type tested 400KV GIS has passive busbar design. We meet the requirement of service continuity, maintenance & repair without provision of any barrier in busbar. All the requirement of repair & maintenance as per specifications are met with passive non-segregated busbar design. This design is accepted by various utilities in India and Abroad. This type of passive non-segregated busbar design is working satisfactorily at site without any issues hence we request an acceptance of this design. | Refer our reply already given to the similar queries in Clarification-I. |
| General Topics |  |  |  |  |
| 21 | KPS-2 400kV GIS Busduct Extension | Pressure difference between existing and present scope GIS. | There is a difference in rated SF6 filling pressure across different OEMs. Hence to integrate existing GIB with new OEM GIB, requesting PGCIL to allow to fill SF6 gas inside extension adaptor at a pressure nearly matching existing GIB rated pressure | Refer our reply already given to the similar queries in Clarification-I. |
| 22 |  | Floor level at KPS-2 S/s | We require section view of the switchyard to assess floor level. We are assuming flat surface without any elevation/decline. Kindly confirm. | Refer our reply already given to the similar queries in Clarification-I. |
| 23 |  | Online PD monitoring / online Gas monitoring | We assume no online PD monitoring/ Gas monitoring is required. Kindly confirm. | Refer our reply already given to the similar queries in Clarification-I. |
| Section Project |  |  |  |  |
| 24 | 2.3 | 400kV: 400kV line is to be connected in existing 400kV Line Bay Module provided with interface module brought out of GIS Hall in existing diameter comprising of LWSR(F)-Tie-Line. | We understand Interface module brought out of GIS Hall in existing diameter have isolating link and terminated with Gas tight bushing by existing supplier. We also require drawing and gas pressure details of exisiting GIB to check our adaptor compatibility. | Refer our reply already given to the similar queries in Clarification-I. |
| BoQ |  |  |  |  |
| 25 |  | Annexure-S11, 245 kV Gas Insulated Switchgear (Double Main Busbar Scheme) > i) GIS Bus bar Module: | For Rajgarh 220kV ICT bay, As per BOQ and section project, GIS Busbar module is asked with VT and earth switch. However, in tender SLD no such VT/earthing switch is shown. Kindly confirm which document to follow. | Refer Amendment-III. |
| 26 | KPS-2 | GIB to GIB extension adaptor | Extension adaptor not mentioned in BOQ as separate line item. Kindly include the same. | Refer our reply already given to the similar queries in Clarification-I. |