| Sl. No. | Details as per Technical Specification Document No / Clause No / | Description as per Bid Document | Bidder’s Query / Clarification | POWERGRID’s Reply |
| --- | --- | --- | --- | --- |
| 01 | Technical Specification, Section– Project, Rev.00 Clause 8.6 | Requirement & validity of Dynamic short circuit test on 105MVA (400/√(3))/ (220/√ (3))/ 33kV 1-Ph Autotransformer: - “Dynamic short circuit test once conducted successfully on 105MVA, (400/√(3))/ (220/√(3))/ 33kV 1-Ph Autotransformer, shall be acceptable.” - Bidder / Manufacturer should have successfully carried out Dynamic Short Circuit test on 105MVA or above rating 400/220/33kV or 400/230/33kV, 1-Phase Auto transformer as on the originally scheduled date of bid opening and shall enclose the relevant Test Report/certificate along with bid. Design review of offered 400kV Class Auto transformer shall be carried out based on the design of short-circuit-tested 105MVA or above rating 400/220/33kV or 400/230/33kV, 1-Phase Auto transformer. In case manufacturer has not successfully carried out Dynamic Short Circuit test on 105MVA or above rating 400/220/33kV (or 400/230/33kV), 1-Phase Auto transformer as on the originally scheduled date of bid opening, the same shall be carried out successfully on 105MVA (400/√ (3))/ (220/√ (3))/33kV 1-Phase Transformer, before supply of the Transformer & Cost of Dynamic Short Circuit test shall be on account of bidder only. | …. intends to participate in subject tender of Powergrid. In reference to the section project for requirement of DSC on 105 MVA 1PH Auto-Transformer, BHEL have credentials for 315 MVA 3ph ICT DSC. In this regards, it is requested to consider our 315 MVA 3PH ICT DSC credentials in lieu of DSC requirement ON 105MVA 1PH Auto-Transformer. Requesting you kind confirmation on the above thereby enabling us to participate in this tender. …………… | Refer Amendment No.-II |
| 02 | Technical Specification, Section– Project, Rev.00 Clause 8.6 | Requirement & validity of Dynamic short circuit test on 105MVA (400/√(3))/ (220/√ (3))/ 33kV 1-Ph Autotransformer: - “Dynamic short circuit test once conducted successfully on 105MVA, (400/√(3))/ (220/√(3))/ 33kV 1-Ph Autotransformer, shall be acceptable.” - Bidder / Manufacturer should have successfully carried out Dynamic Short Circuit test on 105MVA or above rating 400/220/33kV or 400/230/33kV, 1-Phase Auto transformer as on the originally scheduled date of bid opening and shall enclose the relevant Test Report/certificate along with bid. Design review of offered 400kV Class Auto transformer shall be carried out based on the design of short-circuit-tested 105MVA or above rating 400/220/33kV or 400/230/33kV, 1-Phase Auto transformer. In case manufacturer has not successfully carried out Dynamic Short Circuit test on 105MVA or above rating 400/220/33kV (or 400/230/33kV), 1-Phase Auto transformer as on the originally scheduled date of bid opening, the same shall be carried out successfully on 105MVA (400/√ (3))/ (220/√ (3))/33kV 1-Phase Transformer, before supply of the Transformer & Cost of Dynamic Short Circuit test shall be on account of bidder only. | This has reference to above cited subject. We are pleased to inform you that we are keen to participate in above reference mentioned tender. Our design team is working on same. But for optimized design we need more time As per the tender condition we request you to please accept SC Test of our existing 315 MVA, 400 KV 3 phase against Fresh SC test requirement of 105 MVA, 400KV single phase design review and approval. ……………… | Refer Amendment No.-II |