| Sl. no. | REF. TO SECTION/ VOLUME | Clause No | Existing provision of bidding documents | To be Amended as |
| --- | --- | --- | --- | --- |
| 1 | Volume -II (Technical Specifications) |  | Technical Specification: Section -Transformer (Upto 400kV Class) C/ENGG/MODEL-SPEC/TRF Rev 13, Page 55 of 10 Technical Particulars / Parameters of Transformers (220/132 3-Phase Auto Transformer) | Replaced with Annexure-U : Technical Particulars / Parameters of Transformers (220/132/33 kV 3-Phase Auto Transformer) |
| 2 | Volume -II (Technical Specifications) | Section-Project Clause no. 2.1.1.7 | Augmentation of Fire protection System: - Complete in all respect including HVWS & Hydrant system for 1x 200MVA,220/132/33kV,3-Ph Auto Transformer (ICT-4). The piping for fire protection system shall be extended from nearest available header tapping point. - The existing Fire Protection Annunciation Panels shall be used for signals from Fire protection system for 200MVA 220/132/33KV Auto Transformer (ICT-4) under present scope. Contractor shall integrate the annunciation/alarm signals of 1x200MVA, 220/132/33kV, Auto Transformer with the existing Annunciation panels & the scope shall include Capability enhancement as required & all necessary items i.e cards (annunciation card) , cables for which cost is deemed to be included against BPS line item of FIRE PROTECTION-220KV, 200MVA, 3PH T/F. | - HVWS & Hydrant system for 1x 200MVA,220/132/33kV,3-Ph Auto Transformer (ICT-4), complete in all respect. The piping for fire protection system shall be extended from nearest available header tapping point. - DELETED |
| 3 | Volume -II (Technical Specifications) | Section-Project Clause no. 2.1.1.7 | New Clause added : | Supply of new Fire Detection & Alarm Panel shall be covered under present scope. Dismantling of existing Fire Protection alarm Panel ( Make : Vijay Industries and Projects limited) is included under present scope & no additional payment is to be made under this account. Existing Power & signal/control Cables are all envisaged for re-use for the scope. The scope shall also include one to one replacement with existing panel in all respect. All necessary hardware including cabling, integration, glands, connector etc required for above work is deemed to be included against BPS line item of FIRE DETECTION & ALRAM PANEL for CRB. Additional Power signal/control Cables for incorporation of the 220/132 KV, 200 MVA New Transformer shall be under present scope. |
| 4 | Volume -III (Bid Form And Price Schedules) | New Item in Bid Price Schedule -1, 2 | NIL (NEW ITEM ADDED) | S.No; Activity Description; Item Description; Material Code; Unit; Qty. 01; FIRE FIGHTING SYSTEM; Fire Detection and Alarm System for Control Room Building(220kV); 1000012013; SET; 1. |
| 5 | Volume -III (Bid Form And Price Schedules) | New Item in Bid Price Schedule -3 | NIL (NEW ITEM ADDED) | S.No; Activity Description; Item Description; Material Code; Unit; Qty. 01; FIRE FIGHTING SYSTEM; Fire Detection and Alarm System for Control Room Building(220kV); 100002057; SET; 1. |
| 6 | Volume -III (Bid Form And Price Schedules) | Second Envelope Bid, Vol.-III of the Bidding Documents | Existing File “Price_schedule” | The existing file “Price_schedule” Stand replaced as “Price_schedule_rev_01” |