| **Query No** | **Clause Number/Subject** | **Description of Query by the Bidder** | **Clarification** |
| --- | --- | --- | --- |
| 1. | 1.1.3 of Technical Specification, Volume-II of bidding document | 1.We have following chillers available with us  •Chiller Capacity – 9.5 Tr at 35 Degree Ambient with R407C (Green Refrigerant)  •Chiller Capacity – 23 Tr at 35 Degree Ambient with R407C (Green Refrigerant) is the next available capacity.  Please let us know which one to quote. | The Bidder is required to supply chiller unit of minimum 10 TR complying with the technical specification. |
| 2. | Technical Specification, Volume-II of bidding document | Heating system is required or not during the winter period, please clarify, same is not given in the BOQ. | Heating System is required. Please Refer to Sl. No 2. of BOQ |
| 3. | Technical Specification, Volume-II of bidding document | Chiller will be placed on the Convertor hall Roof only, please clarify. | Chiller shall be placed on converter hall roof. |
| 4. | Technical Specification, Volume-II of bidding document | System will be installed as per BOQ or as per Tender document, please clarify. | BOQ is in line with the other provisions of the bidding Document. |
| 5. | Scope of work Under AMC contract/Technical Specification | In case of shell & tube type compressor, tube brushing is not possible. | The offered compressor should meet the requirement of as specified in the Technical Specification. For De-scaling in condenser tubes or any other section of chiller unit Manual/Chemical/or equivalent method may be used. |
| 6. | Scope of work Under AMC contract | Additional Cost will be charged for Top Up refrigerant.-Carrying out testing of lubricant & water once in a year. | No additional payment shall be made against top up of refrigerant within warranty period of 5 years. |
| 5. | Scope of work Under AMC contract | In case of 3Ph Compressor only one year warranty is given. 3 years will cover in AMC & additional 2 years will be charged extra. | The offered compressor shall be of minimum 5 Years warranty in line with provisions of the bidding document. |

**NOTE: Bidder is requested to visit Vindhyachal Substation for better understanding and clarity of scope of work and its easy implementation.**