| Sl. No. | # Volume/ Section/ Description | # Clauses | # Bidder’s Query | # POWERGRID Reply |
| --- | --- | --- | --- | --- |
| Volume-II: Technical Specifications |  |  |  |  |
|  | 2.1 Extension of 400/220kV Rajgarh Substation | (iv) 220kV Outdoor GIS Bus Duct, 220kV SF6-to-Air Bushings for connecting to existing 220kV AIS Bus I & Bus II and connection arrangement using 220kV Bus Post Insulators. | Please confirm the type of conductor used for the Main Buses. | Please refer the tender drawing No. C/ENGG/WR/VAHJAYIN/RAJGARH-EXTN/SLD/01 for type of conductor. |
|  | 3.1 I a. Extension of 415V ACDB at Rajgarh Substation | Extension of both sections of existing 415 Volt ACDB panel through 2 nos. new PVC Cables each (3.5Cx70Sq m) by providing new 415 V ACDB extension panels. Scope includes providing 2 x Incoming feeder modules (125Amp, 4P MCCB) at Existing ACDBs (One Module at each Section). | The bidder understands that the vacant module with busbar is available for fixing of 2 nos. 125A, 4P MCCB at the existing ACDB. Please confirm. | Confirmed |
|  | 3.1 I b. Extension of 220V DCDB-1 & 220V DCDB-2 at Rajgarh Substation | Extension of both sections of existing 220V DCDB-1 & 220V DCDB-2 panel through 2 nos. new PVC Cables each (2Cx150Sq m) by providing new 220V DCDB extension panels. Scope includes providing 2 x Incoming feeder modules (63Amp, 4P MCCB) at Existing DCDBs (One Module at each DCDB). | The bidder understands that the vacant module with busbar is available for fixing of 2 nos. 63A, 4P MCCB at the existing DCDB. Please confirm. | Confirmed |
|  | 2.2 Extension of 765/400/220kV Pune (Sikrapur) GIS Substation | 012120-E-IS-SY-GL-1023, Rev-B 765KV PUNE (NEW) SUBSTATION OVERALL EARTHING LAYOUT | The earthmat layout and Cable trench layout of Pune Substation is not available in the tender documents as per Annexure - 1. Kindly provide the same. | The required Drawings shall be shared to successful bidder during Detail Engineering. Bidders are to visit the sites if required. |
|  | 2.2 Extension of 765/400/220kV Pune (Sikrapur) GIS Substation |  | The bidder understands that the new ICT yard will be located adjacent to the existing spare ICT. The gap as shown in the layout need not to be considered. Please confirm our understanding. | The location of 765KV ICT bank under present scope is to be considered as per tender drawing and gap as shown in the layout need to be considered. . However, the exact location of 765KV ICT bank under present scope shall be finalized during detail engineering |
|  | Extension of 132/66kV Gangtok Substation: | Transformer bay | Based on the site visit, one(1) no. 132/66kV 50MVA transformer is already placed in uncharged condition above plinth in the space earmarked in the tender layout for new CT/LA/Gantry tower for the current scope of 132/66kV transformer no.3. We understand that the space marked in the tender layout will be cleared and vacated area will be handed over to bidder prior to carrying out curent scope of work for 50MVA transformer bay. Please confirm. | Necessary area will be handed over to bidder prior to carrying out current scope of work for 50MVA transformer. |
|  | Extension of 132/66kV Gangtok Substation: | Dismantling of 132kV, 600A Current transformer | The bidder understands that the dismantled CT (as is where is basis) will be handed over to the storage area within the substation premises only. Please confirm. | Dismantled CT will be handed over to the storage area within the substation premises. |
|  | Extension of 132/66kV Gangtok Substation: | General | The bidder understands that at Gangtok substation, space for temporary laydown area, store, site office shall be provided by M/s PGCIL. | Space for temporary laydown area, store, site office shall be under the scope of the bidders. |
|  | Extension of 132/66kV Gangtok Substation: | General | The bidder understands that at Gangtok substation, necessary space for disposal of excavated earth / debris shall be provided by M/s PGCIL. | Necessary space for disposal of excavated earth / debris shall be under the scope of the bidder. |
|  | Raigarh Pune and Gangtok |  | During the site visit, the bidder has observed that there is a scope of dismantling of drain, cable trench and road for augementation work. Further we also understand that, reconstruction of dismantled drain, cable trench, road shall be covered by various main heads of schedule -3, Civil work. Please confirm our understanding for Rajgarh, Pune and Gangtok site. | Bidding document is ample clear. Bidders are to quote accordingly. |
|  | Cl no. 7.0 | Order of precedence : In case of any discrepancy between Section-PROJECT, Section-GTR and other technical specifications on scope of works, Section-PROJECT shall prevail over all other sections. In case of any discrepancy between Section-GTR… | In case of discrepancy in scope, rating and requirement between Section Project and Bid Price schedule, we understand bidder to follow & quote as per bid price schedule. Please confirm. | Confirmed. However, the rating of equipment in BPS is to be read in line with Section-Project / Technical specification |
|  | Extension of 132/66kV Gangtok Substation: CL 3.3.1 / D (ii) Price_schedule: EXTN OF 132/66KV GANGTOK SS Sl.no 24,25,26,27 | Bidder to supply the Control Panel (Duplex Type) for each of 132kV & 66kV side of Transformer bay under present scope. The present scope of control panels shall place in control room, along with existing control and relay panels | During site visit, we observed that adequate space for installation of following panels is not available: 2 Nos Duplex control panel for 132kV & 66KV side transformer. 2 Nos Simplex relay panel for 132kV & 66kV side transformer. The bidder understands that adequate space shall be provided to the bidder in the control room building for placing the panels. | Space shall be provided to the bidder in the existing control room building for placing the panel & this shall be finalized during detail engineering. |
|  | Extension of 132/66kV Gangtok Substation: CL 3.3.1 / D (iv) | The existing 132kV Busbar protection relay make & model is Easun Reyrolle RP-DAD3.1 (Single main & Transfer Bus Scheme- 87M & 87T). Bidder’s scope includes augmentation of Busbar protection for bays under present scope of work. Supply of Analog Cards as well as Digital I/O cards, necessary wiring/cabling, modification of configuration, connections and integration for completion of bus bar protection system etc. for the purpose of augmentation is included under present scope | As per section project , the existing busbar protection relay is of Easun Reyrolle RP-DAD3.1. We understand it is a low impedance centralized bus bar protection relay. Also kindly clarify the specified relay is not obsolete and serviceable. | Bidding document is ample clear. Bidders are to quote accordingly. |
|  | Clause No. 25, page no. 48 of 79 | After the GIS Switchgear has been fully installed at site and SF6 gas filled at rated filling density, the complete assembly shall be subjected to the site tests as per IEC-62271-203 and POWERGRID Asset Management Controlled Document No: D-3-01-09-01-01. After the above, Special Dielectric test (Switching Impulse test) shall be conducted for 765 kV GIS with the test voltages specified below:- | The bidder understands that since765 kV GIS switchgear is not in scope and only GIB and bushings needs to be provided, switching Impulse test is not required as mentioned in the specifications. Please confirm. | Bidding document is ample clear. Bidders are to quote accordingly. |
|  | General | - | We understand that PGCIL will authorize the bidder to do the necessary X ray / measurements (including associated de-gassing if needed) on existing GIS to allow design of the interface. Please confirm. Further necessary degassing / opening of existing GIS Bus enclosure for measuring the interface requirement (if required) and during interface will be done by the bidder as required. Subsequently the HV test shall only be carried out on the installed new GIS bays and shall not be carried out on existing GIS. Please confirm. | POWERGRID will authorize the bidder to do the necessary X ray / measurements (including associated de-gassing if needed) on existing GIS to allow design of the interface in the presence of representative of OEM of existing GIS. No additional payment shall be admissible against deputation OEM of existing GIS as required against design requirement as above. |
|  | Clause No. 2.2.1 (ii) | 400 kV GIS ICT bay : 1 No. | We have conducted site visit to assess Extension Work at Pune Substation. Based on the site visit, there is no space available for extension of 400kV Bay under present scope. Also 2 no. 400kV Bays which need to be installed before installation of the proposed bay is also not available at site. The bidder understands that since Extension of 400kV GIS building at Pune substation is not in the present scope of the bidder as per tender conditions, hence we understand that suitable building extension and installation of 2 no. 400kV GIS Bays shall be completed before commencement of proposed work at Pune Substation with sufficient space for installation of 1 no. 400kV Bay. Please confirm. Further bidder also understands that any work related to HVAC, Fire Fighting, Illumination, and other building accessories for the building extension part is also excluded from the bidder's present scope. Please confirm. | Space for present scope of 400kV GIS ICT module l will be provided by POWERGRID. |
|  | Clause No. 5.27, page no. 7 of 79 | In addition to above suitable portable scissor lift shall be provided for access of distant portion of GIS installation. | The bidder understands that since only extension of GIS bays is to be done at Pune site and outdoor GIS is to be provided at Gangtok, hence we understand that Scissor lift shall not be applicable for Pune and Gangtok substations. We understand that Scissor lift is to be considered only at 220kV Rajgarh GIS Substation. Please confirm. | Scissor lift is to be considered only at 220kV Rajgarh GIS Substation under present scope. |
|  | Clause No. 2.3.1(iii) Construction of new 132kV TBC (new) bay - 1 No. (Outdoor GIS) |  | As per the scope of work defined in the tender documents, the bidder needs to do the Supply & ETC of 1 No. - 145KV, 800A, 31.5 KA, SF6 GIS TBC BAY MODULE. Kindly note that as per the provision shown in the Tender Drawing No (GA_Gangtok SS ERES30&33), received along with the tender documents and further based on the site visit, we understand that there is space & access constraint at the site for installation of the 145kV TBC bay module. Also as per the drawing, no separate bay space is allocated for the installation of the 145kV TBC Bay Module. We understand that the ETC and associated civil work has to be carried out at the site based on the technical feasibility and electrical/physical clearances available at the site and the same may require longer shutdown requirement at the site. Also no modification of the existing tower and gantry is envisaged and the same are suitable for mounting additional beam as per tender scope. The bidder understands that necessary consideration and provisions to facilitate the ETC and associated civil work for installation of 1 no. 145kV TBC bay Module has been taken care of by M/s PGCIL and the bidder needs to execute the work as per the scope of work defined in the BPS and tender drawings provided only. Please confirm. | Proposed area for installation of 145kV O/D GIS for TBC Bay module is marked in the GA drawing provided along with tender documents. No modification envisaged in existing Tower/Gantry located near area proposed for installation of 145kV O/D GIS for TBC Bay module. Bidder to quote as per BPS and technical specification. |