| Sl. No. | # Volume/ Section/ Description | # Clauses | # Bidder’s Query | # POWERGRID Reply |
| --- | --- | --- | --- | --- |
| Volume-II: Technical Specifications |  |  |  |  |
|  | General | Testing and Maintanence kit not mentioned | We would like to inform you that in Section Project or BPS document, Testing & Maintanence kit is not mentioned for Pune 765/400kV GIS, Please clarify we need to consider or not. | Bidding document is ample clear. Bidders to quote as per Biddings document. |
|  | GIS Rev-5A Gangtok project | CT module | We would like to inform you that our GIS module for 145kV & 72.5kV GIS is three phase single enclosure module, so we will provide all CT core in single enclosure. Please accept the same. | Confirmed |
|  | GIS Rev-5A Gangtok project | CT ratio | We would like to inform you CT ratio of 66kV GIS is not mentioned in BPS or any document, For 132kV GIS CT ratio 800-400/1A or 600-300/1A available in Rev-5A document. Please clarify which type of ratio of CT to consider for 132kV GIS and Please provide CT details for 66kV GIS. | "TECHNICAL PARAMETERS FOR CURRENT TRANSFORMERS"- ANNEXURE-3 of Technical Specification Gas Insulated Switchgear shall be applicable for 66KV CTs, with following considerations: Rated voltage, Um (kVrms): 72.5KV Rated Primary Current (A): 600/300A Rated dynamic current: 63KA |
|  | SLD & GA drawing Gangtok project | Dimension of outdoor GIS place. | We would like to inform, we required CAD file of Layout and SLD. Pleas provide the same for layout and SLD preparation. | Required documents in PDF format are already part of Tender Drawing in the bidding document. Bidders are to quote accordingly. |
|  | General | Testing and Maintenance kit not mentioned | We would like to inform you that in Section Project or BPS document, Testing & Maintenance kit is not mentioned for Pune 765/400kV GIS, Please clarify we need to consider or not. | Bidding document is ample clear. Bidders to quote as per Biddings document. |