| # Sl. No. | # Volume/ Section/ Description | # Clauses | # Bidder’s Query | # POWERGRID Reply |
| --- | --- | --- | --- | --- |
| # Volume-I; Conditions of Contract (Doc. Code No. DC-3032-15627, June 2020) |  |  |  |  |
|  | GCC Cl. 18.3.1.4(o), Section-IV: GCC, Volume-I of the Bidding Documents | The Building and Other Construction workers (Regulation of Employment and Conditions of Service) Act 1996 and the Cess Act of 1996: All the establishments who carry on any building or other construction work and employ 10 or more workers are covered under this Act. All such establishments are required to pay cess at the rate not exceeding 2% of the cost of construction as may be modified by the Government. The Employer of the establishment is required to provide safety measures at the Building or construction work and other welfare measures, such as Canteens, First-Aid facilities, Ambulance, Housing accommodations for workers near the work place etc. The Employer to whom the Act applies has to obtain a registration certificate from the Registering Officer appointed by the government. | M/s PGCL is requested to deduct the applicable BOCW cess only on service scope of works Panel Erection/Installation, testing and commissioning. The scope of works for supply of equipment’s, software and mandatory spares will be not attracting BOWC cess. Kindly accept the point and confirm. | # The bidders are required to bid as per the provisions of Bidding Documents which are amply clear. |
|  | GCC Clause 20.2.2, GCC, Clause 22, GCC, Section –IV and Final Payment, Clause 1.1 (D) & 1.4, Apendix-1, Sample Form and Procedures | 20.2.2 Operational Acceptance 20.2.2.1 Operational Acceptance shall occur in respect of the Facilities or any part thereof as mentioned below: (I) In case no Functional Guarantees are applicable, Operational Acceptance shall occur when the Facilities or part thereof have been successfully Commissioned and Trial – Operation for the specified period have been successfully completed (II) In case Functional Guarantees are applicable, Operational Acceptance shall occur when the Functional Guarantees are met or the Contractor has paid liquidated damages specified in GCC Sub-Clause 23.3 hereof; or 20.2.2.2 At any time after any of the events set out in GCC Sub-Clause 20.2.2.1 have occurred, the Contractor may give a notice to the Project Manager requesting the issue of an Operational Acceptance Certificate in the form provided in the Bidding Documents or in another form acceptable to the Employer in respect of the Facilities or the part thereof specified in such notice as of the date of such notice. 20.2.2.3 The Project Manager shall within twenty-one (21) days after receipt of the Contractor's notice, issue an Operational Acceptance Certificate. 20.2.2.4 Upon Operational Acceptance, pursuant to GCC Sub-Clause 20.2.2.2, the Project Manager shall issue to the Contractor a Operational Acceptance Certificate as a proof of the final acceptance of the Plant and Equipment. Such certificate shall not relieve the Contractor of any of his obligations which otherwise survive, by the terms and conditions of Contract after issue of such certificate. 20.2.2.5 If within twenty one (21) days after receipt of the Contractor's notice, the Project Manager fails to issue the Operational Acceptance Certificate or fails to inform the Contractor in writing of the justifiable reasons why the Project Manager has not issued the Operational Acceptance Certificate, the Facilities or the relevant part thereof shall be deemed to have been accepted as at the date of the Contractor's said notice. | We understand that the term ‘or any part thereof’ refers to Substation wise completion of work/TOC or operational acceptance. Hence warranty will be applicable substation wise as soon as first substation is completed and TOC is received for the same. Similarly final 15% payment can be paid substation wise within 30 days of Operational Acceptance of corresponding substation. | Provisions of Bidding Documents are amply clear. |
|  |  | 22. Defect Liability 22.1 The Contractor warrants that the Facilities or any part thereof shall be free from defects in the design, engineering, materials and workmanship of the Plant and Equipment supplied and of the work executed. 22.2 Unless otherwise specified in SCC, the Defect Liability Period shall be twelve (12) months from the date of Taking Over /Completion of Facilities (or any part thereof). If during the Defect Liability Period any defect should be found in the design, engineering, materials and workmanship of the Plant and Equipment supplied or of the work executed by the Contractor, the Contractor shall promptly, in consultation and agreement with the Employer regarding appropriate remedying of the defects, and at its cost, repair, replace or otherwise make good (as the Contractor shall, at its discretion, determine) such defect as well as any damage to the Facilities caused by such defect. The Contractor shall not be responsible for the repair, replacement or making good of any defect or of any damage to the Facilities arising out of or resulting from any of the following causes: (a) improper operation or maintenance of the Facilities by the Employer (b) operation of the Facilities outside specifications provided in the Contract (c) normal wear and tear. 22.3 The Contractor‟s obligations under this GCC Clause 22 shall not apply to (a) any materials that are supplied by the Employer under GCC Sub-Clause 17.2, are normally consumed in operation, or have a normal life shorter than the Defect Liability Period stated herein (b) any designs, specifications or other data designed, supplied or specified by or on behalf of the Employer or any matters for which the Contractor has disclaimed responsibility herein (c) any other materials supplied or any other work executed by or on behalf of the Employer, except for the work executed by the Employer under GCC Sub-Clause 22.7. 22.4 The Employer shall give the Contractor a notice stating the nature of any such defect together with all available evidence thereof, promptly following the discovery thereof. The Employer shall afford all reasonable opportunity for the Contractor to inspect any such defect. 22.5 The Employer shall afford the Contractor all necessary access to the Facilities and the Site to enable the Contractor to perform its obligations under this GCC Clause 22. The Contractor may, with the consent of the Employer, remove from the Site any Plant and Equipment or any part of the Facilities that are defective if the nature of the defect, and/or any damage to the Facilities caused by the defect, is such that repairs cannot be expeditiously carried out at the Site. 22.6 If the repair, replacement or making good is of such a character that it may affect the efficiency of the Facilities or any part thereof, the Employer may give to the Contractor a notice requiring that tests of the defective part of the Facilities shall be made by the Contractor immediately upon completion of such remedial work, whereupon the Contractor shall carry out such tests. If such part fails the tests, the Contractor shall carry out further repair, replacement or making good (as the case may be) until that part of the Facilities passes such tests. 22.7 If the Contractor fails to commence the work necessary to remedy such defect or any damage to the Facilities caused by such defect within a reasonable time (which shall in no event be considered to be less than fifteen (15) days), the Employer may, following notice to the Contractor, proceed to do such work, and the reasonable costs incurred by the Employer in connection therewith shall be paid to the Employer by the Contractor or may be deducted by the Employer from any monies due the Contractor or claimed under the Performance Security. 22.8 If the Facilities or any part thereof cannot be used by reason of such defect and/or making good of such defect, the Defect Liability Period of the Facilities or such part, as the case may be, shall be extended by a period equal to the period during which the Facilities or such part cannot be used by the Employer because of any of the aforesaid reasons. Upon correction of the defects in the Facilities or any part thereof by repair/replacement, such repair/replacement shall have the Defect Liability Period extended by a period mentioned in GCC Sub-Clause 22.2 from the time of such replacement/repair of the facilities or any part thereof. 22.8.1 At the end of the Defect Liability Period, the Contractor's Liability ceases except for latent defects. The Contractor's liability for latent defects warranty shall be limited to period of ten (10) years from the end of Defect Liability Period. For the purpose of this clause, the latent defects shall be the defects inherently lying within the material or arising out of design deficiency, which do not manifest themselves during the Defect Liability Period defined in this GCC Clause 22, but later. 22.9 Except as provided in GCC Clauses 22 and 29, the Contractor shall be under no liability whatsoever and howsoever arising, and whether under the Contract or at law, in respect of defects in the Facilities or any part thereof, the Plant and Equipment, design or engineering or work executed that appear after Defect Liability Period except for the liability towards obligations that may survive in terms of the Contract after Defect Liability Period, except where such defects are the result of the gross negligence, fraud, criminal or willful action of the Contractor. |  |  |
|  |  | 1. TERMS OF PAYMENT In addition to the Conditions stipulated under GCC Clause 8, the following terms & Conditions will apply. 1.1 Supply Portion …………………. D Final Payment Balance fifteen percent (15%) of the Ex-works price component of the Main Equipment shall be paid within 30 days of Operational Acceptance (on successful completion of system availability tests) and proof of submission of the required no. of reproducibles, O&M manuals, approved drawings, data sheets, test reports, pamphlets and manual of spares, maintenance & testing equipment etc. ………….. 1.4 Supply of Services Portion: (a) Eighty five percent (85%) of the installation charges shall be paid on pro-rata basis after installation at site and on certification by the Employer. Further, one of the conditions for release of first progressive payment / subsequent payment shall be submission of ‘Safety Plan’ alongwith all requisite documents in line with GCC clause on Safety Precaution and proforma provided in this Section – Sample Forms and Procedure and approval of the same by the Engineer In-Charge. (b) Balance fifteen percent (15%) shall be paid within 30 days of Operational Acceptance alongwith the corresponding final payment for supply portion mentioned at Clause C (a) above. |  |  |
| # Volume-II; Technical Specifications (Doc. Code No. DC-3032-15628, June 2020) |  |  |  |  |
|  | Section Project_Rev.00: 11.5 | Firewalls & routers | a. We recommend Firewall & Routers to be proposed as single device Router-Cum-Firewall meeting the project specification, port count & spares ports. b. Kindly confirm number of ports required in total : As per tender we can find total 4 ports of RJ-45 10/100 required in Router and 6 at Behramapore. c. Number of ports required in Firewall not defined ? Also any spares port to be considered in both router & firewall? | a) Firewall & Router can be a single device as per TS. b) 4 nos. Ethernet interfaces of 10/100 Mbps at all stations except Behramapore where 8 nos. Ethernet interfaces of 10/100 Mbps are required in case Router & firewall is a single device c) 4 nos. Ethernet interfaces of 10/100 Mbps at all stations except Behramapore where 6 nos. Ethernet interfaces of 10/100 Mbps are required in firewall in case router & firewall are separate devices |
|  | Section Project_Rev.00: 11.5 | Firewalls & routers | Kindly confirm Firewall & router shall be Industrial Grade & type tested as per Substation environment. | Already replied in Clarification No -1: Provision of TS shall prevail. |
|  | Section Project_Rev.00: 11.5 | Shall support IPv4 and IPv6 address and port inspection and filtering | We shall provide Stateful firewalls for IP address, port numbers for source & destination, source & destination MAC. | Already replied in Clarification No -1: Provision of TS shall prevail. |
|  | Section Project_Rev.00: 11.5 | Shall have capacity to store local logs for at least 6 months which should include system logs, security events logs, application specific logs, routing logs, firewall traffic logs etc. | It depends upon the size of data flowing in the network each day, firewall/ Router in-built have limited memory space. We recommend having different SYSLOG server or SIEM server to maintain data logs. Recommendation is to have dedicated Network Management software(NMS) with syslog and a dedicated hard disk at a centralized location for data storage as memory of Firewall is limited and flash memory | Already replied in Clarification No -1: Provision of TS shall prevail. |
|  | Section Project_Rev.00: 11.5 | Shall have IPSec VPN with AES 128/256/512 encryption and SHA1/128/512 | AES with 128/256 supported SHA1 for 128, as 256 above may be part of NFGW not in Industrial hardware when used as Router & firewall | Already replied in Clarification No -1: Provision of TS shall prevail. |
|  | Section Project_Rev.00: 11.5 | Capability to whitelist the hosts for accessing the firewall | Whitelisting depends upon allowing of particular protocols or usage. Depending upon policy we can define for stateful inspection. | Already replied in Clarification No -1: Provision of TS shall prevail. |
|  | Section Project_Rev.00: 11.5 | Shall support static and dynamic routing in both IPv4 and IPv6 | support for IPv4 available & IPv6 support for Static routing available, with static route source & destination are defined. Dynamic routing for IPv6 is restricted to only enterprise grade hardware, also end device in PGCIL network like BCU, RTU, relays don’t have IPv6 addressing, so we request to allow specs: As IPv4 (static & dynamic) IPv6 (static). Kindly confirm. | Refer Amendment-07 |
|  | Section Project_Rev.00: 11.5 Router | Shall have capacity to store local logs for at least 6 months which should include system logs, security events logs, application specific logs, routing logs, traffic logs etc. | It depends upon the size of data flowing in the network each day, firewall/ Router in-built have limited memory space. We recommend having different SYSLOG server or SIEM server to maintain data logs. Recommendation is to have dedicated Network Management software(NMS) with syslog and a dedicated hard disk at a centralized location for data storage as memory of Firewall is limited and flash memory | Query is repeated. Already replied in Sl.No. 7 |
|  | Section Project_Rev.00: 11.5 | Capability to whitelist the hosts for accessing the router | Whitelisting depends upon allowing of particular protocols or usage. Depending upon policy we can define for stateful inspection. | Already replied in Clarification No -1: Provision of TS shall prevail. |
|  | Section Project_Rev.00: 11.5 | Shall support static and dynamic routing in both IPv4 and IPv6 | Support for IPv4 available & IPv6 support for Static routing available, with static route source & destination are defined. Dynamic routing for IPv6 is restricted to only enterprise grade hardware, also end device in PGCIL network like BCU, RTU, relays don’t have IPv6 addressing, so we request to allow specs: As IPv4 (static & dynamic) IPv6 (static). Kindly confirm. | Query is repeated. Already replied in Sl.No. 10. |
|  | Section Project_Rev.00: 11.5 | The router shall have NERC-CIP compliance for CIP-005 | Please elaborate as CIP-005 is a standard, so it should be allowed as per OEM Firewall & router. Accordingly OEM can submit details how CIP005 is ensured by them through Hardware & network at time of detailed engineering. | Already replied in Clarification No -1: Provision of TS shall prevail. |
|  | Section Project_Rev.00: 11.5 | Firmware should have latest patches available as on commissioning date. Firmware should be upgradable through offline patches | firmware can be reloaded and updated individually, which ensures the patchability of the system. During a firmware update, the device is fully operational . A reboot is required to activate the new patch management process in place according to which documents all firmware releases, feature enhancements, and bug fixes in a traceable manner. Updates are made available by Siemens free of charge. The corresponding installation is usually performed by the system operator or the service technician responsible for system maintenance | Already replied in Clarification No -1: Provision of TS shall prevail. |
|  | Section Project_Rev.00: 11.5 | Firewalls & routers | we have integration with NTAMC network. Pls check which specs are required to be followed if we have to supply for NTAMC, as NTAMC have their own specs for router cum firewall. | Already replied in Clarification No -1: Provision of TS shall prevail. |
|  | RTU Technical Specification_Rev02 : Cl. 1.11 | Data Concentrators | We are again raising the below point as PGCIL has given the response "Bidder to comply the Technical specification". However, ther is contradiction in technical specification. We understand there is no requirement of Data Concentrators in this project. So all RTUs shall have Communication Ports as per Cl. 1.3 & Table-1. | RTU shall have capability to act as Data Concentrator as per Clause 1.11 of RTU Technical Specification. For port requirement, please refer Clause 1.3 and Table - 1 of RTU Technical Specification. |
|  | Amendment No.-05 Clause 11.13 | All equipment/materials/items, as per Annexure-XX, as applicable under present scope of works, shall be procured and supplied from domestic manufacturers only. | We understand that applicable under this tender mentioned in Annexure-XX shall be supplied by domestic manufacurer registered in India. However, the manufacturer if required may import some components to be used in the offerd system and shall specify the imported content in relevant format which are already part of documentation requirement of this tender. kindly confirm | The equipment mentioned at Annexure-XX shall be procured and supplied from domestic manufacturers only meeting the requirements of Technical Specification. |
|  | Amendment No.-05 Clause 11.14 | Any imported equipment/ material /item/ parts/ component to be supplied under the contract shall be tested in the certified laboratories to check for any kind of embedded malware/ Trojans/cyber threats and for adherence to Indian Standards as per the directions issued by Ministry of Power/Govt. of India from time to time. In case of such import from specified “prior reference” countries, the requirement of prior permission from the Govt. of India including protocol for testing in certified and designated laboratories by Ministry of Power/Govt. of India shall also be complied with by the contractor. | Kindly provide the following details as same is not mentioned in the provided documents/amendment: 1.Prior reference countries, 2. Certified labs , 3. Details of standards 4. Type of test as per which device needs to be tested for malware threats. 5. Some of the equipments are imported from our parent works, Germany . Hence request PGCIL to accept the equipment complying to technical specifications. | 1) The “prior reference” countries shall be as per the order dtd-11.08.2020 issued by Ministry of Power with subject- “Clarification regarding “Prior Reference” countries in respect of import of equipments / components / works & services in Power Sector”. 2) The test laboratories shall be as per certification and designation issued by Ministry of Power/Govt. of India. 3) Standards like BIS 16335 shall be referred for testing in conjunction with relevant orders issued by Ministry of Power/Govt. of India. 4) The testing protocol as mentioned in referred clause shall be finalized by Ministry of Power/Govt. of India. 5) The referred clause is applicable to any of the imported equipment/material/item/parts/components to be supplied under the contract. |
|  | Amendment No.-05 Clause 11.15 | The equipment offered by the contractor shall at least conform to the requirements specified under relevant IS standard. In case of discrepancy between IS and other international standard, provisions of IS shall prevail. The Contractor shall also note that the list of standards presented in this specification is not complete. Whenever necessary, the list of standards shall be considered in conjunction with specific IS. If the IS standard is not available for an equipment/material, then other applicable International standard (IEC/Equivalent), as per the specification, shall be accepted.” | Siemens product portfolios are designed/developed as per the internationally harmonized standards and the compliance to the application specific IEC standards are available for every product. Hence it is requested to keep the standard compliance to IEC/IS standard in the specifications. Also can add, Whenever necessary, the list of standards shall be considered in conjunction with specific IS/IEC standards relevant for the product family. | The equipment shall be provided meeting the requirements at specified clause of Technical Specifications. |
|  | RTU Technical Specification | RTU Technical Specification | The Aux RTU in the station shall be completely dismantled and replaced by sets of new RTUs (as per contract). | RTU replacement shall be done for the location mentioned at Appendix A of RTU Technical Specification. |
|  | RTU Technical Specification | RTU Technical Specification | All the cabling shall be done for these Aux RTU as per the Price Schedule items provided. | Bidder to comply the Technical Specification |
|  | RTU Technical Specification | RTU Technical Specification | There shall be no interface for these proposed RTUs with: - NTAMC RTU (which shall be retained and continued to send data to NTAMC Control Centers). - IEDs on IEC-61850/Modbus Protocol. | Bidder to comply the Technical Specification |
|  | RTU Technical Specification | RTU Technical Specification | The proposed New RTU shall be configured for transmitting data to LDC only. | Bidder to comply the Technical Specification |