| # Sl. No. | # Volume/ Section/ Description | # Clauses | # Bidder’s Query | # POWERGRID Reply |
| --- | --- | --- | --- | --- |
| # Volume-I; Conditions of Contract (Doc. Code No. DC-3032-15627, June 2020) |  |  |  |  |
|  | # GCC Clause 9.3.1, SCC, Section –V | Supplementing Sub-Clause GCC 9.3.1 with the following: The Contractor shall, within twenty-eight (28) days of the notification of award, provide a performance security for the due performance of the Contract in the amount equivalent to Ten percent (10%) of the Contract Price (including Maintenance charges during Defect Liability Period and AMC charges after Defect Liability Period), with a validity upto ninety (90) days beyond the Defect liability Period. The same shall be extended by the Contractor from time to time till ninety (90) days beyond the actual Defect Liability Period, as may be required under the Contract. Apart from Performance Security(ies) as mentioned above, the contractor is required to arrange additional Performance Security(ies), for various equipment, if applicable, as per Technical Specifications. The above additional Performance Securities shall be submitted before release of first dispatch payment of respective equipment. The said security(ies) shall be required to be extended from time to time till ninety (90) days beyond the actual Defect Liability Period, as may be required under the Contract. Further, Contractor shall within 28 days, after Defect Liability Period, provide Contract Performance Guarantee in the amount equivalent to Two Percent (2%) of the Total Contract Price to cover the contractor’s obligations under Maintenance Period as per the provisions in the Technical Specification, Vol-II, with a validity upto ninety (90) days beyond the AMC Period, as per Form - 20 of Section – VI: Sample Forms and Procedures. The said security(ies) shall be required to be extended from time to time till ninety (90) days beyond completion period of Annual Maintenance Contract as may be required under the Contract. | As we will have different agreement for AMC, whether we need to include AMC amount in PBG. Also PBG is valid till defect liability period. Please clarify on amount and period. | # The provisions of the Bidding Documents are amply clear. |
|  | # GCC Clause 18.3.3, Section-IV: General Conditions of Contract | # 18.3.3 Safety Precautions # 18.3.3.1 The Contractor shall observe all applicable regulations regarding safety on the Site. # Unless otherwise agreed, the Contractor shall, from the commencement of work on Site until Taking Over, provide: # a) fencing, lighting, guarding and watching of the Works, and # b) Temporary roadways, footways, guards and fences which may be necessary for the accommodation and protection of Employer / his representatives and occupiers of adjacent property, the public and others. # 18.3.3.2 The Contractor shall ensure proper safety of all the workmen, materials, plant and equipment belonging to him or to Employer or to others, working at the Site. The Contractor shall also be responsible for provision of all safety notices and safety equipment required both by the relevant legislations and the Project Manager, as he may deem necessary………………………………………………………………… | Contractor has no responsibility or liability for the pre-existing condition of Purchaser’s equipment or the Site. Prior to Contractor starting any work at Site, Purchaser will provide documentation that identifies the presence and condition of any Hazardous Materials existing in or about Purchaser’s equipment or the Site that Contractor may encounter while performing under this Contract. Purchaser shall disclose to Contractor industrial hygiene and environmental monitoring data regarding conditions that may affect Contractor’s work or personnel at the Site. Purchaser shall keep Contractor informed of changes in any such conditions. | # The provisions of the Bidding Documents are amply clear. |
|  | # GCC Clause 37, Section-IV: General Conditions of Contract | 37. Assignment 37.1 Neither the Employer nor the Contractor shall, without the express prior written consent of the other party (which consent shall not be unreasonably withheld), assign to any third party the Contract or any part thereof, or any right, benefit, obligation or interest therein or thereunder. | Please add the following at the end of the Clause: Nothing herein shall affect the right of the Contractor to assign receivable under the Contract by way of factoring. | # The provisions of the Bidding Documents are amply clear and shall remain unaltered. |
|  | # Clause 1.1 (C.1) (a), Supply Portion, Apendix-1, Sample Form and Procedures | a) Software (Substation Automation System (SAS)) i) Twenty percent (20%)# of the Ex-works price of Software shall be paid on pro-rata basis after successful completion of Factory Tests (FAT) and delivery of software tapes to Employer’s respective sites as identified in the Contract software installation, based on certification by the Employer. # In case the contractor opts not to take interest bearing advance then this payment shall be 30% instead of 20%. ii) Fifty five percent (55%) of the Ex-works price of Software shall be paid on pro-rata basis after successful completion of Field tests, based on certification by the Employer. | Without advance :- 30% on FAT and 55% on completion of Field Test 15% Operational Acceptance. We understand payment will release witin 30 days of FAT and Field tests. Kindly confirm. | # The provisions of the Bidding Documents are amply clear. |
|  | # Clause 1.1 (C.1) (b), Supply Portion, Apendix-1, Sample Form and Procedures | b) Hardware (RTU) i) Sixty percent (60%)^ of the Ex-works price of Hardware (including spares) shall be paid on pro-rata basis on shipment of equipment and on submission of : a) Evidence of dispatch (R/R or receipted L/R). b) Contractor's GST invoice, claim & packing list identifying contents of each shipment. c) Manufacturer’s/Contractor’s guarantee certificate of quality. d) Insurance Policy/Certificate. e) Material Inspection Clearance Certificate (MICC) for dispatch issued by the Employer’s representative. f) Test Certificate. g) The details of items, components, raw materials, services etc. procured/availed from MSEs, if any, for the preceding 6 months, in respect of all the contracts in the respective executing Region of POWERGRID as per format enclosed at Section VI, Forms, Volume-I of the bidding documents. ^ In case the contractor opts not to take interest bearing advance or has opted to take interest bearing initial advance but the advance payment has become inadmissible for the reason specified in 1.1 A above, then this payment shall be 70% instead of 60%. ii) Fifteen (15%) of the Ex-works price of Hardware (including spares) shall be paid on pro-rata basis within 30 days of receipt of equipment at site and on submission of claim and physical verification by the Employer. ** In case the contractor opts not to take interest bearing advance or has opted to take interest bearing initial advance but the advance payment has become inadmissible for the reason specified in 1.1 A above, then this payment shall be 85% instead of 75%. | 70% of Shipment 15% on receipt of material post verification 15% on Operational Acceptance We understand payment will release witin 30 days of FAT and Field tests. Kindly confirm. | # The provisions of the Bidding Documents are amply clear. |
|  | # Clause 1.1 (D), Supply Portion, Apendix-1, Sample Form and Procedures | D Final Payment Balance fifteen percent (15%) of the Ex-works price component of the Main Equipment shall be paid within 30 days of Operational Acceptance (on successful completion of system availability tests) and proof of submission of the required no. of reproducibles, O&M manuals, approved drawings, data sheets, test reports, pamphlets and manual of spares, maintenance & testing equipment etc. | 15% on Operational Acceptance This will be release after last station completion or station wise. Kindly confirm. | # The provisions of the Bidding Documents are amply clear. |
|  | # Clause 1.4, Supply of Services Portion, Apendix-1, Sample Form and Procedures | 1.4 Supply of Services Portion: (a) Eighty five percent (85%) of the installation charges shall be paid on pro-rata basis after installation at site and on certification by the Employer. Further, one of the conditions for release of first progressive payment / subsequent payment shall be submission of ‘Safety Plan’ alongwith all requisite documents in line with GCC clause on Safety Precaution and proforma provided in this Section – Sample Forms and Procedure and approval of the same by the Engineer In-Charge. (b) Balance fifteen percent (15%) shall be paid within 30 days of Operational Acceptance alongwith the corresponding final payment for supply portion mentioned at Clause C (a) above. | 85% on certification + 15% in 30 days post operational acceptance. We propose first Progressive payment clause should be de-linked with the service payment. Kindly confirm. | # The provisions of the Bidding Documents are amply clear. |
|  | # Apendix-1, Sample Form and Procedures | # 1.1 Supply Portion # …………….. # ……………. D Final Payment Balance fifteen percent (15%) of the Ex-works price component of the Main Equipment shall be paid within 30 days of Operational Acceptance (on successful completion of system availability tests) and proof of submission of the required no. of reproducibles, O&M manuals, approved drawings, data sheets, test reports, pamphlets and manual of spares, maintenance & testing equipment etc. ……………… 1.4 Supply of Services Portion: ………………………. (b) Balance fifteen percent (15%) shall be paid within 30 days of Operational Acceptance alongwith the corresponding final payment for supply portion mentioned at Clause C (a) above. ……………. | # Bidder understands that the balance 15% as indicated to be paid within 30 days of Operational Acceptance by the Employer, implies that the payment shall be made on pro-rata basis (substation wise) and Substation wise TOC shall be issued by Employer. Please confirm. | # The provisions of the Bidding Documents are amply clear. |
|  | # Clause 1.7, Supply of Services Portion, Apendix-1, Sample Form and Procedures | 1.7 AMC Charges after Defect Liability Period Annual Maintenance Charges subsequent to Defect Liability Period shall be paid quarterly on furnishing GST invoice(s) for the Annual Maintenance Charges by Contractor and on certification by the Employer in line with provisions of Technical Specifications. | AMC Quarterly payment - We Propose advance Quartely payment for AMC. Kindly confirm. | # The provisions of the Bidding Documents are amply clear. |
|  | # Clause A) (a) (III), Apendix-3 Insurance Requirements, Sample Form and Procedures | (III) The Contractor shall take the policy in the joint names of Employer and the Contractor. The policy shall indicate the Employer as the beneficiary. However, if the Contractor is having an open policy for its line of business, it should obtain an endorsement of the open cover policy from the insurance company indicating that the dispatches against this Contract are duly covered under its open policy and include the name of the Employer as jointly Insured in the endorsements to the open policy. | Insurances in the Joint names of Employer & Contractor specifically for transit Insurance, is not possible as it is common policy. We propose the Insurance Policy is in the Contractor name only. However the primary liabilty is of the contractor to deliver the material at site in Good Condition. Kindly confirm. | # The provisions of the Bidding Documents are amply clear. |
|  | # NUCLEAR USE | ……………… | 'The Material/equipment/services sold by the Supplier are not intended for use in connection with any nuclear facility or activity, and the Purchaser warrants that it shall not use or permit other to use the material/equipment/services for such purpose, without advance written consent of Supplier. If in breach of this, any such use occurs, Supplier (and its parent, affiliate, suppliers and subcontracts) disclaims all liability for any nuclear or other damage, injury or contamination, and, in addition to any other rights of Supplier, Purchaser shall indemnify and hold Supplier (and its parent, affiliates and employees) harmless against all such liability. Consent of Supplier under this section to any nuclear use, if any, will be conditioned upon additional terms and conditions that Supplier determines acceptable for protection against nuclear liability. | # The Material/ equipment / services sold by the Contractor are not intended for use in connection with any nuclear facility or activity. |
|  | # General | …………………. | Purchaser (as an “Indemnifying Party”) shall indemnify the Contractor (as an “Indemnified Party”) from and against claims brought by a third party, on account of personal injury or damage to the third party’s tangible property, to the extent caused by the negligence of the Indemnifying Party in connection with this Contract. In the event the injury or damage is caused by joint or concurrent negligence of Purchaser and Contractor, the loss or expense shall be borne by each party in proportion to its degree of negligence. For purposes of Contractor’s indemnity obligation, no part of the Products or Site is considered third party property. | # The provisions of bidding documents remain unaltered. |
|  | # General | …………………. | The impacts of Coronavirus cannot be reasonably determined at this time. This proposal does not account for any potential adverse impacts of Coronavirus on GE’s performance of obligations. In the event of any delays and adverse impacts, GE reserves the right for an equitable adjustment of the schedule and prices herein to offset the effects of Coronavirus delays. | # The provisions of bidding documents remain unaltered. |
| # Volume-II; Technical Specifications (Doc. Code No. DC-3032-15628, June 2020) |  |  |  |  |
|  | # Section Projects, Detailed Scope of Work Cl.no-4.0 | # Necessary up-gradation of firmware of IED’s if required shall be deemed to be included elsewhere | # Bidder understands that the upgradation of firmware of IEDs refer to the modification (if any) on the Control IEDs only (and not any Protection IEDs) that shall be required to establish the communication with the proposed new SAS/RTU system. # Any changes in the Hardware level for any IEDs under present scope, required during successful commissioning, shall be taken care by Employer. Please confirm our understanding. # Also, we would request the Employer to take the same out of scope as during bidding time it can't be possible to ascertain the exact number of IEDs that will require the upgradation and can only be known at the time of commissioning. # Or else, request Employer to provide the list of IEDs that they presume to be upgraded in Firmware level. | # All IEDs are communicating to existing SAS. It shall be the responsibility of the bidder to integrate all IEDs in upgraded SAS. Any firmware upgradation of Protection IEDs required for this purpose is covered in bidders’ scope. List of IEDs has been attached with Tender documents. Replacement of Protection IEDs is not envisaged in the present scope. |
|  | # Section Projects, Detailed Scope of Work Cl.no-4.0 | # Integration of IEDs with proposed new SAS/RTU | # Bidder understands that the bays as indicated specifically in the Scope of Work section of the Section project, need to be considered. Any bay which are getting extended during this time till commissioning of this contract, shall be however excluded from Bidder's scope. Also, we want in case the same has to be integrated, Employer should provide the bay details with details of IEDs, in addition to those that have been mentioned in the Section Project - Scope of Work. | # For Bay extension work in the substation under separate contract, scope includes SAS Augmentation work. Hence bidder is only required to provide all necessary information for integration of those Bays with the upgraded SAS being provided under present scope by the bidder. |
|  | # Section Projects, Detailed Scope of Work Cl.no-4.0 | # General Query - IEDs if any having compatibility issue on Windows 10 based Software system. | # Bidder understands, if any existing IEDs have compatibility issue with System on Windows 10, apart from the resolution to Bidder's Query against Sl. No. 1) as mentioned, Employer shall correct the same and the same shall not be in the scope of Bidder. | # It shall be the responsibility of the bidder to integrate all IEDs in upgraded SAS. Kindly also refer reply at Sl. No. 1. |
|  | # Section Projects, Detailed Scope of Work Cl.no-4.0 | # General Query | # Bidder request the Employer to provide the details of the following IEDs substation wise: # 1. Number of IEDs & EFS (Station and Bay level) - make, model, FW version and Substation wise. # 2. Any IED available on non-IEC 61850 protocol. | # Tentative list of IEDs has been attached as Annexure-III to Section Project. Further, as per Clause 3.2 of Section – Project, the bidder shall visit the site and acquaint itself with the site conditions. |
|  | # Section Projects, Detailed Scope of Work Cl.no-4.0 | # General Query - DGA/RTCC/Telecom equipment integration into SAS/RTU system. | # Bidder understands that the present IEDs (from DGA/RTCC or Telecom equipment) which are not presently connected to SAS/RTU system shall be connected after proposal of new SAS/RTU system. # In this context, Bidder request the Employer to provide station wise details for these IEDs (which are presently not connected, but proposed to be connected in present scope). # Bidder request Employer whether to consider the hardware (EFS, Patch cord, LIU, etc) for connecting these devices. | # As per Clause 11.8 of Section – Project, the bidder shall integrate these devices. However, bidder shall visit site and acquaint itself with the site conditions. # The additional hardware (EFS & LIU) for connecting these devices are not envisaged for integration of Online DGA & Digital RTCC. Bidder may quote accordingly. |
|  | # Section Project; General Query | # - | # Bidder request the Employer to provide the details of the following during commissioning time: # 1. Communication software for Third party IEDs, with latest compatible version. # 2. Backup for Database for NTAMC RTU # 3. Project Backup files from IEDs. (scd/icd/mcl. Etc) # 4. Architecture and S900 RTU schematic of the existing substations # 5. Signal list for existing C264 & S900 RTU. # 6. Signal list for SAS substations (under present scope). Cabling for bringing any additional signal shall be excluded from the scope of Bidder. | # Same shall be finalized during detailed engineering meeting the requirements of Technical Specification. # Control Cabling for bringing any additional signal is not envisaged. |
|  | # RTU Specification, Clause 1.13.1 # Clause 1.28.2 | # Contact Multiplication Relays # Multi function Transducers | # Bidder request the Employer to confirm the availability of space provision for mounting these items (CMR, MFT, Heavy duty relays) in the Employer's existing Control and Protection panels. # Bidder request Employer for station wise breakup of CPU cards, DI module, DO Module, Analog Module, CMR, MFT, Weather stations, etc as mentioned in the RTU Price Schedule. | # Availability of space for mounting of CMR, MFT, Heavy duty relay in existing panel to be assessed during survey and detailed engineering. Bidder may quote as per the quantity given in BPS. |
|  | # Price Schedule, # Item no. 15) for ER1 RTU replacement # Item no. 17) for ER-2 and Orissa | # Cables for RTU | # Bidder request the Employer to confirm the following: # 1. Substation wise quantity of Control cable requirement for acquiring the Field signals. # 2. Possibility of whether using the part of existing control cables (after dismantling of existing RTU panels) for signal acquisition will be allowed. | # 1. Substation wise quantity of Control cable requirement shall be finalized during survey and detailed engineering. # 2. Bidder to comply Technical Specification |
|  | # RTU Specification | # General Query - Integration of any IEC-61850 IEDs and Supply of EFS in RTU Stations. | # Bidder request Employer to indicate the list of any IEC-61850 IEDs that may be integrated into the proposed new RTU under the present scope. Also, is there any requirement of supplying EFS in order to connect the same in the present scope. | # List of any IEDs/EFS to be integrated shall be provided during detailed engineering. |
|  | # RTU Specification | # General Query - Synchronisation in RTU | # Bidder seeks confirmation whether Synchro-check function shall be required in RTU for the feeders that are to be integrated into the proposed RTU (17 nos. Stations). | # Bidder to comply Technical Specification. |
|  | # Scope of Contract | # Retaining of IEDs which are not specifically brought out in any of the Employer's documents | # Bidder understands that the SAS system which are specifically not brought out in any of the Employer's document (like Bay level EFS, GPS systems, Network LAN, IED to EFS - Bay level connectivity, etc) shall be retained during upgradatation of the SAS systems. Bidder request Employer to ensure healthiness and working condition of these SAS equipment. | # The bidder understanding is generally in order. However Bidder Shall quote as per provisions of BPS and Technical specifications. |
|  | # Section Project; # Detailed Scope of Work ¦ Clause 4.0 | # Complete Data base configuration for Local HMI and remote control center shall be as per data list from PGCIL. | # Bidder understands that data configuration for Remote Control Center shall be excluded (as per Specific Exclusions - Section project, point no. 5b). Please confirm our understanding. | # Data configuration at local end for all Remote Control Centers including validation shall be in the scope of bidder. However supply of remote end hardware and software is excluded from the scope of contract as per Clause 5(b) of Section Project. |
|  | # Scope of Contract | # Mandatory spares for substations where SAS are getting upgraded. | # Bidder understands that under present scope of contract, Mandatory spares are not required to be considered for Stations with proposed SAS upgradation. Please confirm our understanding. | # Bidder shall quote as per BPS. |
|  | # Scope of Contract | # Configuration and/or modification of Third party IEDs. | # Configuration and/or Modification of Third Party IEDs, as required during commissioning for establishing communication with new SAS/RTU shall be in the scope of Employer | # Complete configuration of SAS to integrate all IEDs is covered in present Scope as per TS. |
|  | # Scope of Contract | # Dismantling of existing RTU and SIC panel for new RTU panels. | # Bidder understands that after Dismantling of RTU/SIC Panels, the panels shall be left in the Control Room Area and shifting (to stores/other Employer designated place) shall not be in the scope of Bidder. Please clarify | # Shifting to designated place within the substation shall be deemed included in present scope. |
|  | # Scope of Contract | # Civil Works for installation of new RTU/SAS panels including trench/tray work. | # Bidder understand that any type of major/minor civil work including tray/trench work shall be in the scope of Employer. Please confirm. | # The bidder understanding is generally in order. However dismantling /erection of Panels, Cabling etc. shall be done as per TS. |
|  | # Scope of Contract | # Integration with Equipment/Systems under Warranty. | # During integration/upgradation job, any equipment/system that shall be required to be integrated into new SAS/RTU system and the same if in Warranty, Employer shall employ the respective OEM as required during successful commissioning of the same. | # Complete configuration of SAS to integrate all IEDs is covered in present Scope of bidder as per TS. |
|  | # Scope of Contract | # Failure of any equipment during commissioning | # During integration/upgradation job, any existing equipment/system that fails during establishing the communication, Bidder shall not be held responsible for the said failure. | # Under such cases replacement of faulty part/component /equipment of existing system shall be in the scope of the bidder. |
|  | # Price Schedule | # AMC - Number of visits | # Bidder request Employer to indicate the number of visits (includes routine and emergency/breakdown) required for AMC in 01 year and 06 years as per Price Schedule. | # The visits shall be as per the requirement given in Technical Specification |
|  | # Detailed Scope of Work ¦ Clause 4.0 | # Modification in existing .icd files (GE as well as non-GE IEDs) due to the change in IO Lists (for SAS) and reporting to Masters | # Bidder understands that the modification in any existing icd files of IEDs due to change in updated approved signal List (for respective OEMs) and report to increased number of masters shall be in the scope of Employer. # Please confirm our understanding. # Also, we would request the Employer to take the same out of scope as during bidding time it can't be possible to ascertain the exact number of IEDs that will require the modification in the icd files and can only be known at the time of commissioning. | # Requisite files shall be provided during detailed engineering. However for any modification required, the bidder has to tie up with respective OEM. |
|  | # Detailed Scope of Work ¦ Clause 4.0 | # PC based Gateways in RTU stations | # Bidder request Employer to confirm whether PC based Gateways can be offered in RTU Substations (as being offered as Substation Gateways in SAS substations) | # Bidder to comply the # Technical Specification. |
|  | # Detailed Scope of Work ¦ Clause 4.0 | # Ed-1 SAS | # Bidder request Employer since there are more Ed-1 IEDs in the system, whether Employer accepts and allow Bidder to propose Ed-1 SAS system for Seamless integration of Ed-1 and Ed-2 IEDs. | # Provision of TS shall prevail |
|  | # Section_Project_Rev.00 Page 6/22 | # Dismantling of existing RTU-SIC Panels, Replacement of RTU to BCU based SAS, 220/132 kV Ara Substation | # How many no. of Panels to be Dismantled? Where to shift the dismantled panels? | # There are 4 RTU racks and 1 Aux. BCU Rack. The bidder is advised to visit site and acquaint itself with the site conditions as per Clause 3.2 of Section – Project. However, location for shifting of dismantled panels shall be within the substation and shall be finalized during execution. |
|  | # Section_Project_Rev.00 Page 6/22 | # Distance between SAS and BCU Panels, Replacement of RTU to BCU based SAS, 220/132 kV Ara Substation | # Kindly share the distance between BCU panels and SAS-Control Room. | # The bidder is advised to visit site and acquaint itself with the site conditions |
|  | # General, General, Replacement of RTU to BCU based SAS, 220/132 kV Ara Substation |  | # Existing RTU is used only for LDC communication or for control of the Substation. Is this RTU communicating to NTAMC also. Kindly confirm | # The RTU is being used to control the substation from NTAMC. |
|  | # SLD_Ara, Replacement of RTU to BCU based SAS, 220/132 kV Ara Substation | # 132kV - Line Bays - 4 No's, ICT(LV) - 3 No's, Line Bays(Future) - 4 No's # 220kV - Line Bays - 4 No's, ICT(HV) - 3 No's, Line Bays(Future) - 3 No's, BC - 1 No. | # We understand that ICT-3 is already available with BCU, hence BCU is not required for ICT-3 and only integration to be done. If it is existing, kindly confirm the make. # Kindly confirm whether BCU to be considered for Future Bays in scope. | # Refer Cl. 4.1.1(viii) of section project. The bidder is advised to visit site and acquaint itself with the site conditions. BCU is not envisaged for future Bays |
|  | # Section_Project_Rev.00 Page 6/22, Replacement of RTU to BCU based SAS, 220/132 kV Ara Substation | # Integration of existing C264 RTU's (RTU Racks and Aux BCU Rack) in upgraded SAS Gateways over IEC-61850 protocol | # How many no. of RTU racks are existing which needs to be integrated. Kindly confirm. | # Auxiliary BCU Rack & Racks of other auxiliary system needs to be integrated. |
|  | # Section_Project_Rev.00 Page 6/22, General, Replacement of RTU to BCU based SAS, 220/132 kV Ara Substation |  | # Furniture to place the OWS and DR PC is already available at site and same shall be used. Kindly confirm | # Supply of furniture is not envisaged in present scope. |
|  | # Section_Project_Rev.00 Page 6/22, General, Replacement of RTU to BCU based SAS, 220/132 kV Ara Substation |  | # Ethernet Switch required to connect the Gateways, servers and printers are exisiting. However ethernet switch required for Bay level and station level as mentioned in Price schedule will be considered in scope. Kindly confirm | # Bidder shall quote as per BPS. Also refer Cl. 4.1.1 of section project. |
|  | # Section_Project_Rev.00 Page 6/22, General, Replacement of RTU to BCU based SAS, 220/132 kV Ara Substation |  | # GPS required for time synchronization is not mentioned in the section project where the SCADA are updgraded. Hope the existing GPS to be used. Kindly confirm. | # Supply of GPS is not included in present scope. |
|  | # General, Photograph of Existing Panels, Replacement of RTU to BCU based SAS, 220/132 kV Ara Substation |  | # Since the site survey is not possible in this situation, Kindly share the photograph of existing RTU panels which are available at site. | # As per Clause 3.2 of Section – Project, the bidder shall visit site and acquaint itself with the site conditions. However, bidder can get the desired details through telephonic conversation with respective site with prior intimation to respective RHQ. |
|  | # General, FO Cable, Replacement of RTU to BCU based SAS, 220/132 kV Ara Substation |  | # The scope of Armoured FO cable required for communicaion between BCU panel to SAS. Is it existing or need to consider. Kindly confirm. | # It is included in present scope. Also refer Cl. 4.1.1(xii) of section project |
|  | # Section_Project_Rev.00 Page 6/22 4.1.1(ix), Necessary Upgradation of Firmware of IED's, Replacement of RTU to BCU based SAS, 220/132 kV Ara Substation |  | # We understand all the existing IED's are with IEC61850 protocol which can communicate with SCADA. Kindly confirm any IED's which are not having IEC61850 protocol. If in case of any firmware upgradation required respective OEM to take care. | # Tentative list of IEDs has been attached as Annexure-III to Section Project. The bidder is required to interface all existing IEDs in updated SAS. |
|  | # General, Integration with NTAMC, Replacement of RTU to BCU based SAS, 220/132 kV Ara Substation |  | # Is this station already integrated with NTAMC. Kindly confirm | # Confirmed. |
|  | # General, Storage, Replacement of RTU to BCU based SAS, 220/132 kV Ara Substation |  | # We understand the storage will be provided by PGCIL to place the new BCU panels and other SAS equipments before erection. | # As per Cl 3.1 of Section Project, the same is in the scope of the bidder. |
|  | # Section_Project_Rev.00 Page 7/22 (i) g., Dismantling of existing RTU-SIC Panels, Replacement of RTU to BCU based SAS, 220/132 kV Purnea Substation |  | # How many no. of Panels to be Dismantled? Where to shift the dismantled panels? | # There are 4 RTU Racks and 1 Aux. BCU Rack in the SS. The bidder is advised to visit site and acquaint itself with the site conditions. Dismantled panels shall be shifted to designated place within the substation. |
|  | # Section_Project_Rev.00 Page 7/22, Distance between SAS and BCU Panels, Replacement of RTU to BCU based SAS, 220/132 kV Purnea Substation |  | # Kindly share the distance between BCU panels and SAS-Control Room. | # The bidder is advised to visit site and acquaint itself with the site conditions |
|  | # General, General, Replacement of RTU to BCU based SAS, 220/132 kV Purnea Substation |  | # Existing RTU is used only for LDC communication or for control of the Substation. Is this RTU communicating to NTAMC also. Kindly confirm | # The RTU is being used to control the substation from NTAMC. |
|  | # SLD_Purnea, Replacement of RTU to BCU based SAS, 220/132 kV Purnea Substation | # 220kV - Line Bays - 4 No's, ICT(HV) - 3 No's, BC - 1 No. | # We understand that all the 132kV Bays which are shown in SLD are already with BCU. # Kindly confirm. | # Bidder understanding is generally in order |
|  | # Section_Project_Rev.00 Page 7/22 4.1.2(vii), Integration of existing RTU's (RTU Racks and Aux BCU Rack) in upgraded SAS Gateways over IEC-61850 protocol, Replacement of RTU to BCU based SAS, 220/132 kV Purnea Substation |  | # How many no. of RTU racks are existing which needs to be integrated. Kindly confirm. | # The bidder is advised to visit site and acquaint itself with the site conditions |
|  | # Section_Project_Rev.00 Page 7/22, General, Replacement of RTU to BCU based SAS, 220/132 kV Purnea Substation |  | # Furniture to place the OWS and DR PC is already available at site and same shall be used. Kindly confirm | # Supply of furniture is not envisaged in present scope. |
|  | # Section_Project_Rev.00 Page 7/22, General, Replacement of RTU to BCU based SAS, 220/132 kV Purnea Substation |  | # Ethernet Switch required to connect the Gateways, servers and printers are exisiting. However ethernet switch required for Bay level and station level as mentioned in Price schedule will be considered in scope. Kindly confirm | # Bidder shall quote as per BPS. Also refer Cl. 4.1.2 of section project. |
|  | # Section_Project_Rev.00 Page 7/22, General, Replacement of RTU to BCU based SAS, 220/132 kV Purnea Substation |  | # GPS required for time synchronization is not mentioned in the section project where the SCADA are updagraded. Hope the existing GPS to be used. Kindly confirm. | # Supply of GPS is not envisaged in present scope. |
|  | # General, Photograph of Existing Panels, Replacement of RTU to BCU based SAS, 220/132 kV Purnea Substation |  | # Since the site survey is not possible in this situation, Kindly share the photograph of existing RTU panels which are available at site. | # As per Clause 3.2 of Section – Project, the bidder shall visit site and acquaint itself with the site conditions. However, bidder can get the desired details through telephonic conversation with respective site with prior intimation to respective RHQ. |
|  | # General, FO Cable, Replacement of RTU to BCU based SAS, 220/132 kV Purnea Substation |  | # The scope of Armoured FO cable required for communicaion between BCU panel to SAS. Is it existing or need to consider. Kindly confirm. | # As per Clause 3.2 of Section – Project, the bidder shall visit site and acquaint itself with the site conditions. Also refer Cl. 4.1.2(xii) of section project # Bidder may quote accordingly. |
|  | # Section_Project_Rev.00 Page 7/22 4.1.2(ix), Necessary Upgradation of Firmware of IED's, Replacement of RTU to BCU based SAS, 220/132 kV Purnea Substation |  | # We understand all the existing IED's are with IEC61850 protocol which can communicate with SCADA. Kindly confirm any IED's which are not having IEC61850 protocol. If in case of any firmware upgradation required respective OEM to take care. | # Tentative list of IEDs has been attached as Annexure-III to Section Project. The bidder is required to interface all existing IEDs in updated SAS. |
|  | # General, Integration with NTAMC, Replacement of RTU to BCU based SAS, 220/132 kV Purnea Substation |  | # Is this station already integrated with NTAMC. Kindly confirm | # Confirmed. |
|  | # General, Storage, Replacement of RTU to BCU based SAS, 220/132 kV Purnea Substation |  | # We understand the storage will be provided by PGCIL to place the new BCU panels and other SAS equipments before erection. | # As per Cl 3.1 of Section Project, the same is in the scope of the bidder. |
|  | # General, Furniture, Upgradation of SAS, All |  | # Furniture to place the OWS and DR PC is already available at site and same shall be used. Kindly confirm | # Supply of furniture is not envisaged in present scope. |
|  | # General, Ethernet Switch, Upgradation of SAS, All |  | # Ethernet Switch, patch cord and KVM required to connect the Gateways, servers and printers are exisiting. Kindly confirm | # Bidder shall quote as per BPS. Also refer Cl. 4.1.4(viii) of section project. |
|  | # General, GPS, Upgradation of SAS, All |  | # The existing GPS to be used for Time synchronization. Kindly confirm. | # Confirmed. |
|  | # General, General, Upgradation of SAS, All |  | # PGCIL to share the existing Backup of .icd files, Architecture and signal list available | # Requisite details shall be provided during detailed engineering. However for any modification required, the bidder has to tie up with respective OEM. |
|  | # General, General, Upgradation of SAS, All |  | # It is understood that the existing IED's/Devices which are already communicating to existing SCADA to be communicated to the new SCADA. There is no new devices to be integrated. Kindly confirm. | # Please also refer to Clause 11.8 of Section Project |
|  | # General, General, Upgradation of SAS, All |  | # We understand all are existing SAS station and SAS panels are already available. The hardwares in the existing panels shall be replaced with new and same panel shall be retained. Where the new panel to be considered and in which SS the dismantling of panel required to be clarified. | # Wherever feasible existing panels can be reutilized. However if it is not possible due to any reason, the supply of same is included in scope of bidders. Bidders are advised to visit the site to acquaint with existing site conditions. Final call shall be taken during detailed engineering. |
|  | # General, General, Upgradation of SAS, All |  | # We understand all the existing IED's are with IEC61850 protocol which can communicate with BCU and SCADA. If in case of any upgradation required, please confirm. | # Tentative list of IEDs has been attached as Annexure-III to Section Project. The bidder is required to interface all existing IEDs in updated SAS. |
|  | # General, General, Upgradation of SAS, All |  | # Is there any Modbus devices to be integrated with new SCADA. Kindly confirm. | # Modbus devices available are reporting to RTU. The same shall be integrated with SAS by integrating the RTU. |
|  | # General, Database configuration for Local HMI and Remote control center, Upgradation of SAS, All |  | # Databse configuration upto Gateway will be included in scope and shall be sent data to RCC in 104 Protocol. However configuration at RCC is not in our scope. Kindly confirm. | # Data configuration for all Remote Control Centers at local end including validation shall be in the scope of bidder. However supply of remote end hardware and software is excluded from the scope of contract as per Clause 5(b) of Section Project. |
|  | # 02_Second Envelope Bid Vol-III_Pkg-Y, SAS Upgradation package in ER-I, Upgradation of SAS, All |  | # As per BOQ, 4 No's of Bay Ethernet Switch to supplied. Kindly clarify on the Type and no. of ports required. | # These have been envisaged for Ara and Purnea SS and number of ports shall be based on final architecture. Same shall be finalized during detailed engineering meeting the requirements of Technical Specifications. |
|  | # Section_Project_Rev.00, Ethernet Switches & LIUs to connect IEDs to Bay level LAN, Upgradation of SAS, All |  | # Ethernet Switches and LIU's required for Bay level are existing. Kindly confirm. However ethernet switches mentioned in BOQ, will be supplied as per price schedule. | # Bidders shall quote as per BPS and scope of work specified against each substation. |
|  | # Section_Project_Rev.00 Clause : 4.5.1, SAS based Substation (Talcher HVDC):, Protocol Converter, Talcher HVDC |  | # Kindly clarify whether the SAS is existing at Talcher and Any upgradation of SAS is required. | # Scope of work is defined in Clause 4.5.1 and SAS details are attached at Annexure-III to Section Project |
|  | # Section_Project_Rev.00 Clause : 4.5.1, Upgradation of Firmware of IED's, Protocol Converter, Talcher HVDC |  | # We understand all the existing IED's are with IEC61850 protocol and already communicating till gateway and it is sending data to remote control center in IEC101 Protocol. Hence there is no upgradation of firmware required. Kindly confirm | # Bidder understanding is generally in Order. However all data is to be made available through protocol converter as per the scope of work |
|  | # Section_Project_Rev.00 Clause : 4.5.1, Ethernet Switches & LIUs to connect IEDs to Bay level LAN, Protocol Converter, Talcher HVDC |  | # Ethernet Switches and LIU's required for Bay level are existing. Kindly confirm. | # Bidder understanding is generally in Order. |
|  | # Section_Project_Rev.00 Clause : 4.5.1, Total Datapoints, Protocol Converter, Talcher HVDC |  | # Kindly share the complete signal list which is already configured in the existing gateway. Support required from PGCIL in case of any OEM Support is required. | # Same shall be handed over during detailed engineering meeting the requirement of Technical Specifications. |
|  | # Section_Project_Rev.00 Clause : 4.5.1, 6 remote control centers, Protocol Converter, Talcher HVDC |  | # The 6 No. of remote control centers will be similar or unique. | # The RCCs at RLDCs and NTAMC shall be different. |
|  | # General, General, RTU Retrofitting, All |  | # Existing RTU is used only for LDC communication or for control of the Substation. Is this RTU communicating to NTAMC also. Kindly confirm | # Bidders may carry out site survey. |
|  | # RTU Technical Specification_Rev02 Clause 1.0, RTU and SIC panel, RTU Retrofitting, All | # The supplied RTUs shall be interfaced with the Control & Relay (C&R) panels, Communication equipment, Power supply distribution boards; for which all the interface cables shall be supplied by the Contractor. | # We understand this is the retrofitting of RTU and already the required cables will be available till the RTU panel from CRP. Kindly confirm | # Bidder to comply the # Technical Specification. |
|  | # RTU Technical Specification_Rev02 Clause 1.0, RTU Panels, RTU and SIC panel, RTU Retrofitting, All |  | # The RTU panels are existing at site and the new RTU to be retrofitted in the existing panels. Kindly confirm | # RTU panel is to be supplied by the bidder & price to be quoted under the item RTU base equipment |
|  | # RTU Technical Specification_Rev02 Clause 1.2 Clause (i), RTU shall have dual redundant CPU and Power Supply unit., RTU and SIC panel, RTU Retrofitting, All |  | # The dual power supply and redundant processor to be accomodated in the single rack. Kindly confirm. | # This shall be finalized during the detailed engineering |
|  | # RTU Technical Specification_Rev02 Clause 1.5, Modems, RTU and SIC panel, RTU Retrofitting, All |  | # The modems required to communicate with Master station is already available. However only the modems specified in Pricing schedule to be supplied. Kindly confirm. | # Bidder to comply the # Technical Specification. |
|  | # RTU Technical Specification_Rev02 Clause 1.9, The RTU shall use the IEC 61850 protocol for communication with IEDs/Numerical Relays over Sub-station LAN, RTU and SIC panel, RTU Retrofitting, All |  | # How many no. of IED's will be connected to each RTU. Support required from PGCIL to get the Signal list and .icd file from other OEM make relays. We understand the existing IED's are already communicating with existing RTU. Kindly confirm | # The number of IEDs/ Numerical relay connected to RTU shall be finalized during detailed engineering. |
|  | # RTU Technical Specification_Rev02 Clause 1.23, RTU and SIC panel, RTU Retrofitting, All |  | # As per pricing schedule 3 No's of SIC panel to be considered in scope to mount the MFT's, Interposing relays etc.. Kindly confirm in which Substation this SIC to be considered. In other Substations, we understand the CMR's and MFT's will be mounted in existing CRP. | # This shall be finalized during the survey and detailed engineering |
|  | # RTU Technical Specification_Rev02 Clause 1.24, Field Implementation, RTU Retrofitting, All | # All cabling between component units of the RTU, RTU to interface cabinet, RTU to MFTs and to the Owner control and relay panels (located in the substation control room) shall be supplied and installed by the Contractor | # We understand this is the retrofitting of RTU and already the required cables will be available till the RTU panel from CRP. Kindly confirm | # Bidder to comply the # Technical Specification. |
|  | # RTU Technical Specification_Rev02 Clause 1.0, Field Implementation, RTU Retrofitting, All |  | # Any cabling required from field to Control room is not in our scope. Kindly confirm. | # Bidder to comply the # Technical Specification. |
|  | # RTU Technical Specification_Rev02 Page 32/38, Energy Meter Communication, RTU Retrofitting, All |  | # It is mentioned that RTU should have two ethernet port for IED and energy meter communication. However, the energy meters supports Modbus protocol as per the detail provided. Kindly confirm any converted required for energy meter communication. | # This shall be finalized during detailed engineering. |
|  | # RTU Technical Specification_Rev02 Page 31/38, Master Station Communication, RTU Retrofitting, All |  | # As per specification, the RTU should have 6 Ethernet ports for master sttion communication. Kindly confirm whether the 6 No. of master Stations will be similar or unique. | # Unique |
|  | # '02_Second Envelope Bid Vol-III_Pkg-Y' Bid Price Schedule: # Sch-1_PR Line Item No. 370 | # Cables for RTU | # Cables for RTU mentioned in LOT. As presently conducting detailed surveys is not possible due to Travel & quarantine restrictions under Corona panedmic, we are unable to access the quanity. So to enable us proper cost consideration please quantify the volume and types of cables required. | # Quantity and type of cable shall be finalized during the survey and detailed engineering |
|  | # '02_Second Envelope Bid Vol-III_Pkg-Y' Bid Price Schedule: # Sch-3_ | # Installation Charges: BCU and its interfacing with NTAMC SCADA | # We understand that Supply of BCU and its integartion/Interfacing work with New supplied/upgraded SAS system not in Existing NTAMC SCADA. Kindly confirm. | # Bidder understanding is generally in order and is as per Annexure –II of Section Project. |
|  | # '02_Second Envelope Bid Vol-III_Pkg-Y' Bid Price Schedule: # Sch-3_44, 67, 90 | # Integration of RTU with Control Centres (Main & Back-up) of IEC104/101 | # We understand that bidder's scope is integration at substation end only. Any work at Remote end (Main Control Centre and Back up control center) is not in bidder's scope. Kindly confirm. | # Data configuration for Remote Control Centers at local end including validation is in the scope of bidder. However supply of remote end hardware and software is excluded from the scope of contract as per Clause 5(b) of Section Project. |
|  | # '02_Second Envelope Bid Vol-III_Pkg-Y' Bid Price Schedule: # Sch-4b # PR activity no. 30 | # AMC for RTU (ER-1): Integration of New Bays…....at RTU site (Similary for ER-II and Odisha Region) | # As per Instruction Sheet we understand any type of AMC is not to be quoted. However if AMC is required - # Kindly clarify the scope of PR activity no. 30, mention the time line of this requirement; whether during Commissioning period, Warranty or after warranty period. | # The AMC is in the scope of contract. # The time line shall be inclusive of all period i.e. Commissioning period, warranty period (1 year) and after warranty period (6 years) |
|  | # '02_Second Envelope Bid Vol-III_Pkg-Y' Bid Price Schedule: # Sch-1_PR Line Item No. 37, 72, 108 | # SIC (System Interface Cabinet: Requirements 1 QTY | # As per Price Bid Schedule Quantity of SIC is mentioned as 1 no. for multiple RTUs. Please Confirm. | # Bidder to comply the # Technical Specification. |
|  | # Section Project_Rev.00 | # Integration of existing IEDs/RTU to new SAS | # We understand that Engineering Database with configuration software of all existing IEDs to generate new ICD files is available the employer. Please Confirm | # Bidder understanding is generally in order. Requisite details shall be provided during detailed engineering. However for any modification required, the bidder has to tie up with respective OEM. |
|  | # Section Project_Rev.00 | # Integration of existing IEDs to new SAS | # Employer will support the bidder in coordinating with the OEM of existing equipment to facilitate the successful integration. Please confirm. | # Bidder to comply the TS. |
|  | # Section Project_Rev.00 | # Integration of existing IEDs to new SAS # Replacement of existing/defective devices not mentioned in the price bid schedule in not in bidder scope. | # We understand that only those devices which are in healthy condition and have proper backup data can be integrated. In case device is not healthy same shall be replaced by the employer. Please confirm. | # All IEDs are communicating to existing SAS. It shall be the responsibility of the bidder to integrate all IEDs in upgraded SAS. Any firmware upgradation of IEDs required for this purpose is covered in bidders’ scope. List of IEDs has been attached with Tender documents. Replacement of Protection IEDs is not envisaged in the present scope. |
|  | # RTU Technical Specification_Rev02 : Cl. 1.3 | # Communication Ports | # We understand that all 17 RTUs shall have communication ports as specified in Cl. 1.3 of the technical specification including CPU redundancy. | # Bidder to comply the Technical specification |
|  | # RTU Technical Specification_Rev02 : Cl. 1.11 | # Data Concentrators | # We understand there is no requirement of Data Concentrators in this project. So all RTUs shall have Communication Ports as per Cl. 1.3 & Table-1 | # Bidder to comply the Technical specification |
|  | # RTU Technical Specification_Rev02 : Cl. 1.22 | # Quantity of Ios | # Bid price schedule indicates quantity of I/O cards along with channel density. We envisage that this includes 20% wired spares as per RTU specification. Kindly clarify and confirm. | # Confirmed |
|  | # RTU Technical Specification_Rev02 : Cl. 1.2 | # "RTU shall support downloading of RTU database from the master station using on IEC 60870-5-101and IEC 60870-5-104 protocol." | # Kindly note that database download from remote location shall be possible only on ethernet interface. Kindly confirm. | # Kindly refer Amendment No-03. |
|  | # General | # SLD/System Architecture | # Kindly provide the SLD and latest system architecture of substations where existing RTU to be replaced. | # This shall be discussed and provided at the time of detailed engineering as required. |
|  | # General | # Civil Work | # We understand that any Civil work(apart from erection of panel & its base), Trench formation is not in Present scope. Kindly confirm. | # The bidder understanding is generally in order. However dismantling /erection of Panels, Cabling etc. shall be done as per TS. |
|  | # General | # Cabling | # Kindly confirm where RTU is to be replace, cabling, re-wiring from CRP/Field to new supplied RTU is also in present scope. | # Bidder to comply the Technical specification |
|  | # Section_Project_Rev.00_Rev.00 | # Supply of SAS Panels | # Please confirm the requirement of Gateway and SAS Panel? Do we need to supply new panels or existing SAS panels can be reutilized? | # Wherever feasible existing panels can be reutilized. However if it is not possible due to any reason, the supply of same is included in scope of bidders. Bidders are advised to visit the site to acquaint it with existing site conditions. |
|  | # Section Project_Rev.00 | # Upgradation of SAS | # AS per section project, supply of Hardware (Gateway, HMI, Server, EWS) is in scope for SAS upgradation. Kindly confirm whether existing Hardware can be utilised and bidders will provide necessary software for upgrade the existing system. | # The scope of supply has been clearly defined for each substation in TS and the same is to be followed. |
|  | # Section Project_Rev.00 | # Upgradation of SAS | # AS per section project, we understand for upgradation existing Software license can be upgraded. For this upgrade PGCIL will support in sending old software dongle against which latest version licenses will be provided | # If possible, existing software licenses without disrupting the functioning of the substation can be utilised |
|  | # Section Project_Rev.00: 11.8 | # Third Party items Integration | # Third party items shall be integrated with SAS: we understand that necessary Service support shall be arranged by PGCIL. | # Complete configuration of SAS to integrate all IEDs is covered in present Scope of the bidder as per TS. |
|  | # Section Project_Rev.00 | # Ethernet Switches | # We understand wherever Ethernet Switches are not specified in Bid Price Schedule for Upgradation of SAS there No new Ethernet Switches are required to be supplied by the bidder, and existing Ethernet Switches and LAN shall be utilized. Please confirm. | # The scope of supply has been clearly defined for each substation in TS and the same is to be followed. |
|  | # RTU Spec Cl. 1.23 | # Dismantling of RTU Panel | # We understand that as per cl. 1.23 dismantling of the RTU panels is in bidder scope. We understand that after removal of the old panel same will handed over to the employer's substation in-charge. Thereafter employer will make necessary shifting arrangement of old panel. | # Since the Project is of replacement of existing RTUs and Dismantling of existing RTUs & accessories shall be in the scope of works. The existing system after dismantling shall be taken away by the contractor and this factor may be taken into consideration while quoting the price bid. This is as per the scope given in clause 1.23 RTU specification_Rev02 |
|  | # Section Project_Rev.00 | # Storage Space | # We understand the employer will provide the suitable locked space in each substation for safe storage of material supplied under this project. | # As per Cl 3.1 of Section Project, the same is in the scope of the bidder. |
|  | # Section Project_Rev.00 # 4.1.1 | # 220/132 KV ARA substation | # For 220/132 KV ARA substation ( conversion of RTU based substation to BCU based substation) . We understand that the existing Dongfang RTUs which are to be replaced were acting as Data Concentrator cum Gateway . The individual Feeder signals to be integrated in the BCUs and the Gateway to be configured in the 2 Nos. IPGCs. Please confirm. | # The scope of work has been clearly defined for each substation in TS and the same is to be followed. |
|  | # Section Project_Rev.00 # 4.1.1 |  | # 1. Is communication to NTAMC to be retained in 220/132KV ARA after BCU based SAS upgradation. Please confirm. # 2. The C264 RTUs in Ara Substation is mainly acting as a Auxiliary RTU for integration of the Substation Auxiliaries. Please confirm. | # The scope of work has been clearly defined for each substation in TS and the same is to be followed. You are also advised to refer Clause 8 of Section Project |
|  | # Section Project_Rev.00 # 4.1.1.v # 4.1.2.v | # (ARA): Supply of Bay Control Unit (BCU) Intelligent Electronic Devices (IEDs) for # control and monitoring as per BOQ for 220kV & 132kV Bays with necessary BCU # panels. # (Purnea): Bay Control Unit (BCU) Intelligent Electronic Devices (IEDs) for control and monitoring as per BOQ for 220kV system with necessary BCU panels. | # Kindly Confirm: # i. Total no. of BCUs to be supplied for the bays as applicable. # Ii. Whether the A/R functionality shall be the part of New BCUs or A/R scheme is already existing in some other protection IED. # Iii. Can we provide multiple BCUs in a panel, with this we can optimize some panel count or one BCU panel per Bay is required? # iv. Alternate option can be the mounting of BCUs in the respective bay panels if the space is available in them, this option will be more feasible w.r.t the individual bay specific cable termination. | # BCU with A/R Functionality shall be supplied. # Provisions of TS shall be followed |
|  | # Section Project_Rev.00 # 4.1.2.v | # GIS Drawings | # For Purnea, GIS drawings to be provided to finalize the BI/BOs. | # Requisite details shall be provided during detailed engineering. |
|  | # Section Project_Rev.00 # 4.1.1.i.a | # “Supply and Installation of 2 Nos Gateway for remote monitoring and control via industrial grade hardware (to RCC) through Secure IEC 60870-5-104 protocol” | # Communication can be secured from router cum firewall level using VPN, hence Secure IEC 104 as built in function of SAS Gateway shall not be required. Kindly clarify and confirm. | # Provision of TS shall prevail. |
|  | # Section Project_Rev.00 # 4.1.1.iii & iv | # "Redundant managed switched Ethernet Local Area Network communication infrastructure with hot standby for Station level and Bay level” | # We understand existing Managed Ethernet Switched Network will be used for all location where SAS is to be upgraded. # For 2 Locations in ER-1 where RTU System is to be upgraded in BCU based SAS there RSTP based single ring network is to be provided. Please confirm. | # The scope of work has been clearly defined for each substation in TS and the same is to be followed. |
|  | # Section Project_Rev.00 # 4.1.1.i | # SAS Upgradation | # For s/s having existing SAS, section project asks for supply & installation of 2x gateways, 2x HMI, 2x servers, 1x DR/EWS, inverters, printers etc. # We envisage that new SAS is not required for these s/s and existing SAS needs to be upgraded. | # The scope of work has been clearly defined for each substation in TS and the same is to be followed. |
|  | # Section Project_Rev.00 # 4.1.1.vi | # NTAMC Gateway | # We understand that all these s/s have existing NTAMC C264 gateways. These are to be integrated in SAS, however connectivity to NTAMC will still remain through C264 gateway. Kindly confirm if our understanding is correct. | # The scope of work has been clearly defined in TS and the same is to be followed. You are also advised to Refer to clause 8 of Section Project |
|  | # Section Project_Rev.00 # 8. BASIC REFERENCE DRAWINGS | # “All existing NTAMC signals including that mentioned in previous line must be configured in upgraded SAS gateways and same IEC104 addresses of signals is to be maintained as per NTAMC signal list to have minimum disruption in operation during upgradation." | # We envisage that NTAMC gateways are to be integrated with SAS over IEC 61850 and hence IEC104 addresses can’t be used. Kindly clarify and confirm. | # The scope of work has been clearly defined in TS and the same is to be followed. You are also advised to Refer to clause 8 of Section Project |
|  | # Section Project_Rev.00 | # Necessary up-gradation of firmware of IED’s if required shall be deemed to be included elsewhere. | # Kindly clarify if required, firmware upgradation will be in bidder’s scope or PGCIL’s scope. | # It has been clearly mentioned in TS that the same is in Bidder’s scope. |
|  | # Section Project_Rev.00 | # Approved Vendor List | # Kindly provide approved vendor list for – ethernet switches, router cum firewall, MFT, etc. | # Same is available at Powergrid Website |
|  | # Section Project_Rev.00 | # Remote HMI | # We understand the remote IGPC supply and configuration for the RCC is not included in our present scope. Kindly Confirm. | # Data configuration for Remote Control Centers including validation shall be in the scope of bidder. However supply of remote end hardware and software is excluded from the scope of contract as per Clause 5(b) of Section Project. |
|  | # Section Project_Rev.00 | # NTAMC Gateway/RTU | # For the Non-SAS based Substations like Birpara and Siliguri , we understand the bay level managed switches are not envisaged and NTAMC BCUs and NTAMC RTUs shall be connected directly to the Station level managed Ethernet Switches. We understand that our proposed PAS servers for the local SAS implementation shall be connected to the Station level managed E/S . Kindly confirm. | # You are advised to Refer to clause 8 of Section Project |
|  | # Section Project_Rev.00 | # NTAMC Gateway/RTU | # As per section project 2 Nos. proposed Firewalls cum Gateway shall be used with the proposed gateway and 2 Nos. existing firewall cum router for existing NTAMC communication to be retained . Kindly inform if 2 parallel communication are to be maintained. # Do we understand here that the old NTAMC RTUs would still communicate on IEC-101 and the new PC based gateways shall be over secured IEC-104 communication . please confirm. | # You are advised to Refer to clause 8 of Section Project |
|  | # Section Project_Rev.00: 11.5 | # Firewalls & routers | # We recommend Firewall & Routers to be proposed as single device Reouter-Cum-Firewall meeting the project specification. Kindly confirm. | # Provision of TS shall prevail. |
|  | # Section Project_Rev.00: 11.5 | # Firewalls & routers | # Kindly confirm Firewall & router shall be Industrial Grade & type tested as per Substation environment . | # Provision of TS shall prevail. |
|  | # Section Project_Rev.00: 11.5 | # Shall support IPv4 and IPv6 address and port inspection and filtering | # We shall provide Stateful firewalls for IP address, port numbers for source & destination, source & destination MAC. | # Provision of TS shall prevail. |
|  | # Section Project_Rev.00: 11.5 | # Shall have capacity to store local logs for at least 6 months which should include # system logs, security events logs, application specific logs, routing logs, firewall # traffic logs etc. | # it depends upon the size of data flowing in the network each day, firewall/ Router in-built have limited space. We recommend to have s different SYSLOG server or SIEM server to maintain data logs. | # Provision of TS shall prevail. |
|  | # Section Project_Rev.00: 11.5 | # Shall have IPSec VPN with AES 128/256/512 encryption and SHA1/128/512 | # AES with 128/256 supported SHA1 for 128, as 256 above may be part of NFGW not in Industrial hardware when used as Router & firewall | # Provision of TS shall prevail.. |
|  | # Section Project_Rev.00: 11.5 | # Capability to whitelist the hosts for accessing the firewall | # this can be done by operating system tools of servers for whitelists | # Provision of TS shall prevail. |
|  | # Section Project_Rev.00: 11.5 | # Shall support static and dynamic routing in both IPv4 and IPv6 | # support for IPv4 available & IPv6 support for Static routing available, with static route source & destination are defined. # Dynamic routing for IPv6 is restricted to only enterprise grade hardware, also end device in PGCIL network like BCU, RTU, relays don’t have IPv6 addressing, so we request to allow specs: # As IPv4 (static & dynamic) IPv6 (static). # Kindly confirm. | # Provision of TS shall prevail. |
|  | # Router | # Shall have capacity to store local logs for at least 6 months which should include # system logs, security events logs, application specific logs, routing logs, traffic # logs etc. | # Since its depends upon the size of data flowing in the network each day, firewall/ Router in-built have limited space. # We recommend to have s different SYSLOG server or SIEM server to maintain data logs. Kindly confirm. | # Provision of TS shall prevail. |
|  | # Section Project_Rev.00: 11.5 | # Capability to whitelist the hosts for accessing the router | # This can be done by operating system tools of servers for whitelists. Kindly confirm. | # Provision of TS shall prevail. |
|  | # Section Project_Rev.00: 11.5 | # Shall support static and dynamic routing in both IPv4 and IPv6 | # Support for IPv4 available & IPv6 support for Static routing available, with static route source & destination are defined. # Dynamic routing for IPv6 is restricted to only enterprise grade hardware, also end device in PGCIL network like BCU, RTU, relays don’t have IPv6 addressing, so we request to allow specs: # As IPv4 (static & dynamic) IPv6 (static). Kindly confirm. | # Provision of TS shall prevail. |
|  | # Section Project_Rev.00: 11.5 | # The router shall have NERC-CIP compliance for CIP-005 | # Please elaborate as CIP-005 is a standard, so it should be allowed as per OEM Firewall & router. Accordingly OEM can submit details how CIP005 is ensured by them through Hardware & network at time of detailed engineering. | # Provision of TS shall prevail. |
|  | # Section Project_Rev.00: 11.5 | # Firmware should have latest patches available as on commissioning date. # Firmware should be upgradable through offline patches | # firmware can be reloaded and updated individually, which ensures the patchability of the system. During a firmware update, the device is fully operational . A # reboot is required to activate the new # patch management process in place according to which documents all firmware releases, feature enhancements, and bug fixes in a traceable manner. # Updates are made available by Siemens free of charge. The corresponding installation is usually performed by the system operator or the service technician # responsible for system maintenance | # Provision of TS shall prevail. |
|  | # Section Project_Rev.00: 11.5 | # Firewalls & routers | # we have integration with NTAMC network. Pls check which specs are required to be followed if we have to supply for NTAMC, as NTAMC have their own specs for router cum firewall. | # Provision of TS shall prevail. |
|  | # Section Project_Rev.00 | # NTAMC/BNTAMC/RTMAC End configuration scope | # We understand that bidder's scope is limited to substation end configuration for NTAMC/BNTAMC/RTMAC only. No work at GE NTAMC/BNTAMC/RTMAC end envisaged. | # Data configuration for Remote Control Centers (including RLDCs) including validation shall be in the scope of bidder. However supply of remote end hardware and software is excluded from the scope of contract as per Clause 5(b) of Section Project. |
|  | # Section Project_Rev.00 | # Replacement of S-900 & C264 RTU | # Do we need to replace whole panel or RTU only in existing panel. Kindly confirm. | # Bidder to comply the Technical specification. |
|  | # General | # IED communication protocols details | # Kindly provide the full details of existing IEDs along with communication protocols and I/Os. | # Tentative list of IEDs has been attached as Annexure-III to Section Project. Further, as per Clause 3.2 of Section – Project, the bidder shall visit the site and acquaint itself with the site conditions. |
|  | # General | # RTU Replacement | # For 14 numbers of conventional substations do we need to provide local SAS also. Please clarify | # The LDMS shall be provided as per Technical Specification. # Bidder to comply Technical specification. |
|  | # General | # Existing Schematic Modification | # Kindly confirm any hard wiring and modifications in existing scheme with reference to the signal list of NTAMC/RTAMC/BNTAMC is also in bidder's scope. | # It is included in substations where RTU system is being replaced by BCU system. Bidder is are also advised to refer Cl. 11.8 of Section Project. |
|  | # General | # Point-to Point Testing | # Kindly confirm point to point local/remote end testing of all signals is also in present scope during upgradation of SAS. | # Testing/Commissioning/Validation etc. is included in present scope as per TS. |
|  | # General |  | # In case any cable is found faulty during Installation & Commissioning, please clarify if it would be bidder's responsibility to replace the same. If Yes, quantification of cable would be extremely difficult during survey as these information would not be readily available and testing of each cable is extremely difficult. | # The system is in running state with no such identified faults. If any fault occurs during execution of work, same shall be replaced/rectified by the bidder. |
|  | # Section V SCC 1 | # Time of completion from the date of Notification of Award 21 Months | # Looking at the quantum of work, it is extremely difficult to complete the work in delivery timeline mentioned in the contract. Please increase the Project Timeline | # Timeline shall be followed |
|  | # Section V SCC 1 | # Time of completion from the date of Notification of Award 21 Months | # In case of delay in outage availability during Testing, we understand Delivery Extension shall be provided by Employer. Please confirm. | # Provision of GCC shall prevail |
|  | # General | # As built Drawings | # We understand As-built drawings are available at each site. Same shall be utilized for Engineering & design works. Please confirm. | # Basic Reference Drawings are attached in Tender. |
|  | # General | # Protocol Compatibility | # We understand that all existing IEDs that are on IEC 61850 communication protocol which are to be integrated with SAS. Kindly confirm. | # All existing IEDs are communicating to existing SAS. It shall be the responsibility of the bidder to integrate all IEDs in upgraded SAS. |
|  | # General | # Signal List | # We understand that PGCIL have final signal List of all substations where SAS to be upgraded. Kindly provide. | # Same shall be shared during detailed engineering |
|  | # General | # Relay replacement scope | # Kindly confirm Is there any requirement of replacing existing relays in case firmware upgradation is not possible or facing dificulties. | # All IEDs are communicating to existing SAS. It shall be the responsibility of the bidder to integrate all IEDs in upgraded SAS. Any firmware upgradation of IEDs required for this purpose is covered in bidders’ scope. List of IEDs has been attached with Tender documents. Replacement of Protection IEDs is not envisaged in the present scope. |
|  | # General | # Control Centre Integration | # for successful Integration of New SAS/RTU with Master & Back-up Control Centres, employer/PGCIL need to provide existing IEC101/104, Telemetry data details like Connection setting & Address, CASDU (Common Address), IOA (Information Object Address), Data Types etc. for all signals to be integrated. | # Same shall be shared during detailed engineering |
|  | # General | # Re-testing of Protection IEDs | # We understand that any kind of Re-testing for Protection after upgrade in Firmware/Modification of Communication Parameters in the relays is not part of scope of work. Kindly confirm. | # Testing for functionality shall be carried out as per Powergrid procedure. |
|  | # General | # Goose Messaging | # We understand that any kind of configuration/modification related to GOOSE messaging in existing IEDs is not part of scope of work. Kindly Confirm. | # Complete configuration of SAS to integrate all IEDs is covered in present Scope as per TS. |
|  | # RTU Technical Specification_Rev02 : Table-1: Technical Particulars of RTU | # Communication Ports | # From Table 1 of the RTU Requirement, we understand that the numbers of communication ports mentioned in table-1 are the total number of ports required in a set of RTU with redundant processors & power supply. Please confirm. | # Bidder to comply the Technical specification. |
|  | # General |  | # Necessary shut-down required for integration of Bays shall be provided by PGCIL. Kindly Confirm. | # Shall be finalized during execution. However all efforts shall be made to minimize the outage. |
|  | # Ara, Implementation of BCU based SAS. Volume II, Part 1 of 5, Section – Project, Rev. 00, Clause:4.1.1, Page 5 & 6 of 22 |  | # Will Power Grid Provide IEC61850 configuration file (SCD file of s/s or CID files for all devices to be integrated on IEC61850) during project execution. | # Requisite details shall be provided during detailed engineering. However for any modification required, the bidder has to tie up with respective OEM. |
|  | # Ara, Implementation of BCU based SAS. Volume II, Part 1 of 5, Section – Project, Rev. 00, Clause:4.1.1, Page 5 & 6 of 22 |  | # Supply of Ethernet switches & Router cum Firewall is it part of scope. | # The scope of work has been clearly defined for each substation in TS and the same is to be followed. |
|  | # Ara, Implementation of BCU based SAS. Volume II, Part 1 of 5, Section – Project, Rev. 00, Clause:4.1.1, Page 5 & 6 of 22 |  | # Can we have details of Mandatory Spares | # Please refer Annexure-II to Section Project |
|  | # Ara, Implementation of BCU based SAS. Volume II, Part 1 of 5, Section – Project, Rev. 00, Clause:4.1.1, Page 5 & 6 of 22 |  | # Following details are required : # 1. IED details of Ara which has to be integrated to SAS. # 2. Overall Panel lay out of s/s. | # Tentative IED details have been attached at Annexure-III. Please refer Amendment No-03. Bidder is also advised to visit site to acquaint itself with site conditions. |
|  | # Ara, Implementation of BCU based SAS. Volume II, Part 1 of 5, Section – Project, Rev. 00, Clause:4.1.1, Page 5 & 6 of 22 |  | # Supplying of BCU (220 kV & 132 kV Bays) in new panel is it acceptable. Is it acceptable. If so we presume control wiring from respective bays would be in the scope of bidder. | # Bidder understanding is generally in order. |
|  | # Ara, Implementation of BCU based SAS. Volume II, Part 1 of 5, Section – Project, Rev. 00, Clause:4.1.1, Page 5 & 6 of 22 |  | # For implementation what would be shut down time provided for Implentation of Upgrdation activity. | # Shall be finalized during execution. However all efforts shall be made to minimize the outage. |
|  | # Ara, Implementation of BCU based SAS. Volume II, Part 1 of 5, Section – Project, Rev. 00, Clause:4.1.1, Page 5 & 6 of 22 |  | # Integration of IEC61850 devices are : # 1. C264 as RTU # 2. BCU & IEDS for ICT3. # Please confirm | # The scope of work has been clearly defined for each substation in TS and the same is to be followed. |
|  | # Ara, Implementation of BCU based SAS. Volume II, Part 1 of 5, Section – Project, Rev. 00, Clause:4.1.1, Page 5 & 6 of 22 |  | # For integration of C264 used as RTU, can we details Model No. Firmware details of C264. | # The bidder is advised to visit site and acquaint itself with the site conditions |
|  | # Ara, Implementation of BCU based SAS. Volume II, Part 1 of 5, Section – Project, Rev. 00, Clause:4.1.1, Page 5 & 6 of 22 |  | # Supply of furniture is it part of the scope | # Supply of furniture is not envisaged in present scope. |
|  | # Ara, Implementation of BCU based SAS. Volume II, Part 1 of 5, Section – Project, Rev. 00, Clause:4.1.1, Page 5 & 6 of 22 |  | # Extension of Power supply from existing ACDB & DCDB in Control room for Powering of supplied device, is it part of scope. | # It is included as per TS |
|  | # Ara, Implementation of BCU based SAS. Volume II, Part 1 of 5, Section – Project, Rev. 00, Clause:4.1.1, Page 5 & 6 of 22 |  | # Supply of Network panel with ethernet switches is part of scope. | # It is included as per TS |
|  | # Purnea, Implementation of BCU based SAS. Volume II, Part 1 of 5, Section – Project, Rev. 00, Clause:4.1.2, Page 7 & 8 of 22 |  | # Will Power Grid Provide IEC61850 configuration file (SCD file of s/s or CID files for all devices to be integrated on IEC61850) during project execution. | # Requisite details shall be provided during detailed engineering. However for any modification required, the bidder has to tie up with respective OEM. |
|  | # Purnea, Implementation of BCU based SAS. Volume II, Part 1 of 5, Section – Project, Rev. 00, Clause:4.1.2, Page 7 & 8 of 22 |  | # Supply of Ethernet switches & Router cum Firewall is it part of scope. | # It is included as per TS |
|  | # Purnea, Implementation of BCU based SAS. Volume II, Part 1 of 5, Section – Project, Rev. 00, Clause:4.1.2, Page 7 & 8 of 22 |  | # Can we have details of Mandatory Spares | # Please refer Annexure-II to Section Project |
|  | # Purnea, Implementation of BCU based SAS. Volume II, Part 1 of 5, Section – Project, Rev. 00, Clause:4.1.2, Page 7 & 8 of 22 |  | # Following details are required : # 1. IED details of Purnea which has to be integrated to SAS. # 2. Overall Panel lay out of s/s. | # Tentative IED details have been attached at Annexure-III. Please refer Amendment No-03. Bidder is also advised to visit site to acquaint itself with site conditions. |
|  | # Purnea, Implementation of BCU based SAS. Volume II, Part 1 of 5, Section – Project, Rev. 00, Clause:4.1.2, Page 7 & 8 of 22 |  | # Supplying of BCU (220 kV Bays) in new panel is it acceptable. Is it acceptable. If so we presume control wiring from respective bays would be in the scope of bidder. | # Bidder understanding is generally in order. |
|  | # Purnea, Implementation of BCU based SAS. Volume II, Part 1 of 5, Section – Project, Rev. 00, Clause:4.1.2, Page 7 & 8 of 22 |  | # For implementation what would be shut down time provided for Implentation of Upgrdation activity. | # Shall be finalized during execution. However all efforts shall be made to minimize the outage. |
|  | # Purnea, Implementation of BCU based SAS. Volume II, Part 1 of 5, Section – Project, Rev. 00, Clause:4.1.2, Page 7 & 8 of 22 |  | # Integration of IEC61850 devices are : # 1. RTU & Aux BCU # 2. BCU & IEDS for 8 No. 132 kV Bays. # Please confirm | # The scope of work has been clearly defined for each substation in TS and the same is to be followed. |
|  | # Purnea, Implementation of BCU based SAS. Volume II, Part 1 of 5, Section – Project, Rev. 00, Clause:4.1.2, Page 7 & 8 of 22 |  | # Clause 4.1.2 calls for integartion of RTU, while Clause 4.2 calls for supply of new RTU Panel. We presume new RTU panel has to be integrated with new SAS. | # These are different scope of work at different substations |
|  | # Purnea, Implementation of BCU based SAS. Volume II, Part 1 of 5, Section – Project, Rev. 00, Clause:4.1.2, Page 7 & 8 of 22 |  | # Supply of furniture is it part of the scope | # Supply of furniture is not envisaged in present scope. |
|  | # Purnea, Implementation of BCU based SAS. Volume II, Part 1 of 5, Section – Project, Rev. 00, Clause:4.1.2, Page 7 & 8 of 22 |  | # Extension of Power supply from existing ACDB & DCDB in Control room for Powering of supplied device, is it part of scope. | # It is included as per TS |
|  | # Purnea, Implementation of BCU based SAS. Volume II, Part 1 of 5, Section – Project, Rev. 00, Clause:4.1.2, Page 7 & 8 of 22 |  | # Supply of Network panel with ethernet switches is part of scope. | # It is included as per TS |
|  | # Sasaram, Implementation of BCU based SAS. Volume II, Part 1 of 5, Section – Project, Rev. 00, Clause:4.1.3, Page 8 & 9 of 22 |  | # Will Power Grid Provide IEC61850 configuration file (SCD file of s/s or CID files for all devices to be integrated on IEC61850) during project execution. | # Requisite details shall be provided during detailed engineering. However for any modification required, the bidder has to tie up with respective OEM. |
|  | # Sasaram, Implementation of BCU based SAS. Volume II, Part 1 of 5, Section – Project, Rev. 00, Clause:4.1.3, Page 8 & 9 of 22 |  | # Supply of Ethernet switches & Router cum Firewall is it part of scope. | # It is included as per TS |
|  | # Sasaram, Implementation of BCU based SAS. Volume II, Part 1 of 5, Section – Project, Rev. 00, Clause:4.1.3, Page 8 & 9 of 22 |  | # We are not clear scope calls for Integration of 400kV bays (Presently integrated in HVDC system), 220kV bays, 132kV bays & 33kV bays in 765kV existing SAS, simulateneosuly scope call for Implementation of new SAS. Can Integration with existing SAS & scope of new SAS be clarified. | # 765kV existing SAS may be read as 765kV upgraded SAS. |
|  | # Sasaram, Implementation of BCU based SAS. Volume II, Part 1 of 5, Section – Project, Rev. 00, Clause:4.1.3, Page 8 & 9 of 22 |  | # Following details are required : # 1. IED details of Sasram which has to be integrated to SAS. # 2. Overall Panel lay out of s/s. # 3. SLD of s/s | # Tentative IED details have been attached at Annexure-III. Please refer Amendment No-03. Bidder is also advised to visit site to acquaint itself with site conditions. |
|  | # Sasaram, Implementation of BCU based SAS. Volume II, Part 1 of 5, Section – Project, Rev. 00, Clause:4.1.3, Page 8 & 9 of 22 |  | # Supplying of New Gateway, Servers in new panel is it acceptable. Is it acceptable. | # Acceptable subject to no installation constraints. Same shall be finalized during detailed Engineering. |
|  | # Sasaram, Implementation of BCU based SAS. Volume II, Part 1 of 5, Section – Project, Rev. 00, Clause:4.1.3, Page 8 & 9 of 22 |  | # For implementation what would be shut down time provided for Implentation of Upgrdation activity. | # Shall be finalized during execution. However all efforts shall be made to minimize the outage. |
|  | # Sasaram, Implementation of BCU based SAS. Volume II, Part 1 of 5, Section – Project, Rev. 00, Clause:4.1.3, Page 8 & 9 of 22 |  | # Integration of IEC61850 devices are : # 1. NTAMC BCU # 2. BCU & IEDS for respective bays. # Please confirm | # The scope of work has been clearly defined for each substation in TS and the same is to be followed. |
|  | # Sasaram, Implementation of BCU based SAS. Volume II, Part 1 of 5, Section – Project, Rev. 00, Clause:4.1.3, Page 8 & 9 of 22 |  | # Clause 4.1.3 calls for integartion of RTU, while Clause 4.2 calls for supply of new RTU Panel. We presume new RTU panel has to be integrated with new SAS. | # These are different scope of work at different substations |
|  | # Sasaram, Implementation of BCU based SAS. Volume II, Part 1 of 5, Section – Project, Rev. 00, Clause:4.1.3, Page 8 & 9 of 22 |  | # Supply of furniture is it part of the scope | # Supply of furniture has not been envisaged in present scope. |
|  | # Sasaram, Implementation of BCU based SAS. Volume II, Part 1 of 5, Section – Project, Rev. 00, Clause:4.1.3, Page 8 & 9 of 22 |  | # Extension of Power supply from existing ACDB & DCDB in Control room for Powering of supplied device, is it part of scope. | # It is included as per TS |
|  | # Sasaram, Implementation of BCU based SAS. Volume II, Part 1 of 5, Section – Project, Rev. 00, Clause:4.1.3, Page 8 & 9 of 22 |  | # Supply of Network panel with ethernet switches is part of scope. | # Acceptable subject to no installation constraints. Same shall be finalized during detailed Engineering. |
|  | # Banka, Lakhisarai, Gaya, Ranchi, Chaibasa, Kishenganj, Daltonganj & Chandwa, Implementation of BCU based SAS. Volume II, Part 1 of 5, Section – Project, Rev. 00, Clause:4.1.4, Page 9 & 10 of 22 |  | # Will Power Grid Provide IEC61850 configuration file (SCD file of s/s or CID files for all devices to be integrated on IEC61850) during project execution. | # Requisite details shall be provided during detailed engineering. However for any modification required, the bidder has to tie up with respective OEM. |
|  | # Banka, Lakhisarai, Gaya, Ranchi, Chaibasa, Kishenganj, Daltonganj & Chandwa, Implementation of BCU based SAS. Volume II, Part 1 of 5, Section – Project, Rev. 00, Clause:4.1.4, Page 9 & 10 of 22 |  | # Supply of Ethernet switches & Router cum Firewall is it part of scope. | # The scope of work has been clearly defined for each substation in TS and the same is to be followed. |
|  | # Banka, Lakhisarai, Gaya, Ranchi, Chaibasa, Kishenganj, Daltonganj & Chandwa, Implementation of BCU based SAS. Volume II, Part 1 of 5, Section – Project, Rev. 00, Clause:4.1.4, Page 9 & 10 of 22 |  | # BCU Details indicated (at Chaibasa) , indicates defective BCU, is supply of defective BCU part of scope. | # Supply of BCU shall be as per BPS. |
|  | # Banka, Lakhisarai, Gaya, Ranchi, Chaibasa, Kishenganj, Daltonganj & Chandwa, Implementation of BCU based SAS. Volume II, Part 1 of 5, Section – Project, Rev. 00, Clause:4.1.4, Page 9 & 10 of 22 |  | # Following details are required : # 1. IED details of Banka which has to be integrated to SAS. # 2. Overall Panel lay out of Banka, Lakhisarai, Gaya, Ranchi, Chaibasa, Kishenganj, Daltonganj & Chandwa s/s. # 3. SLD of Banka, Lakhisarai, Gaya, Ranchi, Chaibasa, Kishenganj, Daltonganj & Chandwa s/s | # List of IEDs and existing SAS architecture has been provided with TS. The bidder is also advised to visit site and acquaint itself with the site conditions |
|  | # Banka, Lakhisarai, Gaya, Ranchi, Chaibasa, Kishenganj, Daltonganj & Chandwa, Implementation of BCU based SAS. Volume II, Part 1 of 5, Section – Project, Rev. 00, Clause:4.1.4, Page 9 & 10 of 22 |  | # For implementation what would be shut down time provided for Implentation of Upgrdation activity. | # Shall be finalized during execution. However all efforts shall be made to minimize the outage. |
|  | # Banka, Lakhisarai, Gaya, Ranchi, Chaibasa, Kishenganj, Daltonganj & Chandwa, Implementation of BCU based SAS. Volume II, Part 1 of 5, Section – Project, Rev. 00, Clause:4.1.4, Page 9 & 10 of 22 |  | # Integration of IEC61850 devices are : # 1. C264 as RTU # 2. BCU & IEDS as inddicated in Bid Document. # Please confirm | # The scope of work has been clearly defined for each substation in TS and the same is to be followed. |
|  | # Banka, Lakhisarai, Gaya, Ranchi, Chaibasa, Kishenganj, Daltonganj & Chandwa, Implementation of BCU based SAS. Volume II, Part 1 of 5, Section – Project, Rev. 00, Clause:4.1.4, Page 9 & 10 of 22 |  | # For integration of C264 used as RTU, can we details Model No. Firmware details of C264. | # The bidder is advised to visit site and acquaint itself with the site conditions |
|  | # Banka, Lakhisarai, Gaya, Ranchi, Chaibasa, Kishenganj, Daltonganj & Chandwa, Implementation of BCU based SAS. Volume II, Part 1 of 5, Section – Project, Rev. 00, Clause:4.1.4, Page 9 & 10 of 22 |  | # Supply of furniture is it part of the scope | # Supply of furniture has not been envisaged in present scope. |
|  | # Banka, Lakhisarai, Gaya, Ranchi, Chaibasa, Kishenganj, Daltonganj & Chandwa, Implementation of BCU based SAS. Volume II, Part 1 of 5, Section – Project, Rev. 00, Clause:4.1.4, Page 9 & 10 of 22 |  | # Extension of Power supply from existing ACDB & DCDB in Control room for Powering of supplied device, is it part of scope. | # It is included as per TS |
|  | # Banka, Lakhisarai, Gaya, Ranchi, Chaibasa, Kishenganj, Daltonganj & Chandwa, Implementation of BCU based SAS. Volume II, Part 1 of 5, Section – Project, Rev. 00, Clause:4.1.4, Page 9 & 10 of 22 |  | # Supply of Network panel with ethernet switches is part of scope. | # Acceptable subject to no installation constraints. Same shall be finalized during detailed Engineering. |
|  | # Biharsharif, Jamshedpur, Purnea, Sasram & Muzaffarpur, Supply of RTU Panels replacing existing RTU. Volume II, Part 1 of 5, Section – Project, Rev. 00, Clause:4.2, Page 10 of 22 |  | # Scope is : # 1. Dismnatling of old RTU Panel (if available). # 2. Supply of new RTU Panel (Replacement of any Field control wiring to RTU Panel is not in scope). # 3. OLTC & MFT Tranducer. # Please confirm | # Bidder to comply the Technical Specification. |
|  | # Biharsharif, Jamshedpur, Purnea, Sasram & Muzaffarpur, Supply of RTU Panels replacing existing RTU. Volume II, Part 1 of 5, Section – Project, Rev. 00, Clause:4.2, Page 10 of 22 |  | # For supplying RTU Panels in line with RTU Specification following details are required: # 1. No. of DI/DO/AI/AO for Biharsharif, Jamshedpur, Purnea, Sasram & Muzaffarpur ss # 2. No. of OLTC Transducer & MFT Transducer for Biharsharif, Jamshedpur, Purnea, Sasram & Muzaffarpur ss | # This shall be finalized during the survey and detailed engineering. |
|  | # Biharsharif, Jamshedpur, Purnea, Sasram & Muzaffarpur, Supply of RTU Panels replacing existing RTU. Technical Specifications for Remote Terminal Units (RTU), Other section Part 1 of 2, Clause:1.3, Page 6 of 38 |  | # Specfication calls for RTU with 6 Ethernet ports on IEC 60870-5-104, if requsite ports are not available is it acceptable if unmanaged switch is supplied to meet the requirement. | # Bidder to comply the Technical Specification. |
|  | # Birpara & Siliguri, Implementation of SAS Upgradation. Volume II, Part 1 of 5, Section – Project, Rev. 00, Clause:4.3.1, Page 10, 11 of 22 |  | # Will Power Grid Provide IEC61850 configuration file (SCD file of s/s or CID files for all devices to be integrated on IEC61850) during project execution. | # Requisite details shall be provided during detailed engineering. However for any modification required, the bidder has to tie up with respective OEM. |
|  | # Birpara & Siliguri, Implementation of SAS Upgradation. Volume II, Part 1 of 5, Section – Project, Rev. 00, Clause:4.3.1, Page 10, 11 of 22 |  | # Supply of Ethernet switches & Router cum Firewall is it part of scope. | # The scope of work has been clearly defined for each substation in TS and the same is to be followed. |
|  | # Birpara & Siliguri, Implementation of SAS Upgradation. Volume II, Part 1 of 5, Section – Project, Rev. 00, Clause:4.3.1, Page 10, 11 of 22 |  | # Following details are required : # 1. IED details of Biprara & Siliguri which has to be integrated to SAS. # 2. Overall Panel lay out of Birpara & Siliguri s/s. | # Tentative IED details have been attached at Annexure-III. Please refer Amendment No-03. Bidder is also advised to visit site to acquaint itself with site conditions. |
|  | # Birpara & Siliguri, Implementation of SAS Upgradation. Volume II, Part 1 of 5, Section – Project, Rev. 00, Clause:4.3.1, Page 10, 11 of 22 |  | # For implementation what would be shut down time provided for Implentation of Upgrdation activity. | # Shall be finalized during execution. However all efforts shall be made to minimize the outage. |
|  | # Birpara & Siliguri, Implementation of SAS Upgradation. Volume II, Part 1 of 5, Section – Project, Rev. 00, Clause:4.3.1, Page 10, 11 of 22 |  | # Integration of IEC61850 devices are : # 1. NTAMC BCU # 2. BCU & IEDS for 132 kV Bays as indicated in Bid Document. # Please confirm | # The scope of work has been clearly defined for each substation in TS and the same is to be followed. |
|  | # Birpara & Siliguri, Implementation of SAS Upgradation. Volume II, Part 1 of 5, Section – Project, Rev. 00, Clause:4.3.1, Page 10, 11 of 22 |  | # Supply of furniture is it part of the scope | # Supply of furniture has not been envisaged in present scope. |
|  | # Birpara & Siliguri, Implementation of SAS Upgradation. Volume II, Part 1 of 5, Section – Project, Rev. 00, Clause:4.3.1, Page 10, 11 of 22 |  | # Extension of Power supply from existing ACDB & DCDB in Control room for Powering of supplied device, is it part of scope. | # It is included as per TS |
|  | # Birpara & Siliguri, Implementation of SAS Upgradation. Volume II, Part 1 of 5, Section – Project, Rev. 00, Clause:4.3.1, Page 10, 11 of 22 |  | # Supply of Network panel with ethernet switches is part of scope. | # New panel is acceptable subject to no installation constraints. Same shall be finalized during detailed Engineering. |
|  | # Berampore, Implementation of SAS Upgradation. Volume II, Part 1 of 5, Section – Project, Rev. 00, Clause:4.3.2, Page 11, 12 of 22 |  | # Will Power Grid Provide IEC61850 configuration file (SCD file of s/s or CID files for all devices to be integrated on IEC61850) during project execution. | # Requisite details shall be provided during detailed engineering. However for any modification required, the bidder has to tie up with respective OEM. |
|  | # Berampore, Implementation of SAS Upgradation. Volume II, Part 1 of 5, Section – Project, Rev. 00, Clause:4.3.2, Page 11, 12 of 22 |  | # Supply of Ethernet switches & Router cum Firewall is it part of scope. | # The scope of work has been clearly defined for each substation in TS and the same is to be followed. |
|  | # Berampore, Implementation of SAS Upgradation. Volume II, Part 1 of 5, Section – Project, Rev. 00, Clause:4.3.2, Page 11, 12 of 22 |  | # Following details are required : # 1. IED details of Berampore which has to be integrated to SAS. # 2. Overall Panel lay out of Berampore s/s. # 3. SLD of Berampore s/s | # IED details are available in Tender documents. The bidder is advised to visit site and acquaint itself with the site conditions |
|  | # Berampore, Implementation of SAS Upgradation. Volume II, Part 1 of 5, Section – Project, Rev. 00, Clause:4.3.2, Page 11, 12 of 22 |  | # For implementation what would be shut down time provided for Implentation of Upgrdation activity. | # Shall be finalized during execution. However all efforts shall be made to minimize the outage. |
|  | # Berampore, Implementation of SAS Upgradation. Volume II, Part 1 of 5, Section – Project, Rev. 00, Clause:4.3.2, Page 11, 12 of 22 |  | # Integration of IEC61850 devices are : # 1. Existing RTU & Aux BCU # Please confirm | # The scope of work has been clearly defined for each substation in TS and the same is to be followed. |
|  | # Berampore, Implementation of SAS Upgradation. Volume II, Part 1 of 5, Section – Project, Rev. 00, Clause:4.3.2, Page 11, 12 of 22 |  | # Supply of furniture is it part of the scope | # Supply of furniture is not envisaged under present scope. |
|  | # Berampore, Implementation of SAS Upgradation. Volume II, Part 1 of 5, Section – Project, Rev. 00, Clause:4.3.2, Page 11, 12 of 22 |  | # Extension of Power supply from existing ACDB & DCDB in Control room for Powering of supplied device, is it part of scope. | # It is included as per TS |
|  | # Berampore, Implementation of SAS Upgradation. Volume II, Part 1 of 5, Section – Project, Rev. 00, Clause:4.3.2, Page 11, 12 of 22 |  | # Supply of Network panel with ethernet switches is part of scope. | # New panel is acceptable subject to no installation constraints. Same shall be finalized during detailed Engineering. |
|  | # New Mali & Rangpo, Implementation of SAS Upgradation. Volume II, Part 1 of 5, Section – Project, Rev. 00, Clause:4.3.3, Page 12, 13 of 22 |  | # Will Power Grid Provide IEC61850 configuration file (SCD file of s/s or CID files for all devices to be integrated on IEC61850) during project execution. | # Requisite details shall be provided during detailed engineering. However for any modification required, the bidder has to tie up with respective OEM. |
|  | # New Mali & Rangpo, Implementation of SAS Upgradation. Volume II, Part 1 of 5, Section – Project, Rev. 00, Clause:4.3.3, Page 12, 13 of 22 |  | # Supply of Ethernet switches & Router cum Firewall is it part of scope. | # The scope of work has been clearly defined for each substation in TS and the same is to be followed. |
|  | # New Mali & Rangpo, Implementation of SAS Upgradation. Volume II, Part 1 of 5, Section – Project, Rev. 00, Clause:4.3.3, Page 12, 13 of 22 |  | # Following details are required : # 1. IED details of New Mali & Rangpo which has to be integrated to SAS. # 2. Overall Panel lay out of New Mali & Rangpo s/s. # 3. SLD of New Mali & Rangpo s/s | # IED details are available in Tender documents. The bidder is advised to visit site and acquaint itself with the site conditions |
|  | # New Mali & Rangpo, Implementation of SAS Upgradation. Volume II, Part 1 of 5, Section – Project, Rev. 00, Clause:4.3.3, Page 12, 13 of 22 |  | # For implementation what would be shut down time provided for Implentation of Upgrdation activity. | # Shall be finalized during execution. However all efforts shall be made to minimize the outage. |
|  | # New Mali & Rangpo, Implementation of SAS Upgradation. Volume II, Part 1 of 5, Section – Project, Rev. 00, Clause:4.3.3, Page 12, 13 of 22 |  | # Integration of IEC61850 devices are : # 1. Existing RTU & Aux BCU # Please confirm | # The scope of work has been clearly defined for each substation in TS and the same is to be followed. |
|  | # New Mali & Rangpo, Implementation of SAS Upgradation. Volume II, Part 1 of 5, Section – Project, Rev. 00, Clause:4.3.3, Page 12, 13 of 22 |  | # Supply of furniture is it part of the scope | # Supply of furniture is not envisaged under present scope. |
|  | # New Mali & Rangpo, Implementation of SAS Upgradation. Volume II, Part 1 of 5, Section – Project, Rev. 00, Clause:4.3.3, Page 12, 13 of 22 |  | # Extension of Power supply from existing ACDB & DCDB in Control room for Powering of supplied device, is it part of scope. | # It is included as per TS |
|  | # New Mali & Rangpo, Implementation of SAS Upgradation. Volume II, Part 1 of 5, Section – Project, Rev. 00, Clause:4.3.3, Page 12, 13 of 22 |  | # Supply of Network panel with ethernet switches is part of scope. | # New panel is acceptable subject to no installation constraints. Same shall be finalized during detailed Engineering. |
|  | # Durgapur, Malda, Binaguri, Subhasgram, Dalkhola, Ganktok & Maithon, Supply of RTU Panels replacing existing RTU. Volume II, Part 1 of 5, Section – Project, Rev. 00, Clause:4.4, Page 13 of 22 |  | # Scope is : # 1. Dismnatling of old RTU Panel (if available). # 2. Supply of new RTU Panel (Replacement of any Field control wiring to RTU Panel is not in scope). # 3. OLTC & MFT Tranducer. # Please confirm | # Bidder to comply the Technical Specification. |
|  | # Durgapur, Malda, Binaguri, Subhasgram, Dalkhola, Ganktok & Maithon, Supply of RTU Panels replacing existing RTU. Volume II, Part 1 of 5, Section – Project, Rev. 00, Clause:4.4, Page 13 of 22 |  | # For supplying RTU Panels in line with RTU Specification following details are required: # 1. No. of DI/DO/AI/AO for Biharsharif, Jamshedpur, Purnea, Sasram & Muzaffarpur ss # 2. No. of OLTC Transducer & MFT Transducer for Biharsharif, Jamshedpur, Purnea, Sasram & Muzaffarpur ss | # This shall be finalized during the survey and detailed engineering. |
|  | # Durgapur, Malda, Binaguri, Subhasgram, Dalkhola, Ganktok & Maithon, Supply of RTU Panels replacing existing RTU. Technical Specifications for Remote Terminal Units (RTU), Other section Part 1 of 2, Clause:4.4, Page 13 of 22 |  | # Specfication calls for RTU with 6 Ethernet ports on IEC 60870-5-104, if requsite ports are not available is it acceptable if unmanaged switch is supplied to meet the requirement. | # Bidder to comply the Technical Specification. |
|  | # Talcher, Protocol Conversion. Volume II, Part 1 of 5, Section – Project, Rev. 00, Clause:4.5.1, Page 13,14 of 22 |  | # Mapping details for conversion for IEC-101 to IEC-104 | # Same shall be finalized during detailed engineering |
|  | # Talcher, Protocol Conversion. Volume II, Part 1 of 5, Section – Project, Rev. 00, Clause:4.5.1, Page 13,14 of 22 |  | # New Redundant Protocol convertor / Gateway would be supplied in a new panel. Please confirm | # New panel is acceptable subject to no installation constraints. Same shall be finalized during detailed Engineering. |
|  | # Talcher, Protocol Conversion. Volume II, Part 1 of 5, Section – Project, Rev. 00, Clause:4.5.1, Page 13,14 of 22 |  | # Supply of Ethernet switches & Router cum Firewall is it part of scope. | # The scope of work has been clearly defined for each substation in TS and the same is to be followed. |
|  | # Jharsuguda, Implementation of SAS Upgradation. Volume II, Part 1 of 5, Section – Project, Rev. 00, Clause:4.5.2, Page 13, 14 of 22 |  | # Will Power Grid Provide IEC61850 configuration file (SCD file of s/s or CID files for all devices to be integrated on IEC61850) during project execution. | # Requisite details shall be provided during detailed engineering. However for any modification required, the bidder has to tie up with respective OEM. |
|  | # Jharsuguda, Implementation of SAS Upgradation. Volume II, Part 1 of 5, Section – Project, Rev. 00, Clause:4.5.2, Page 13, 14 of 22 |  | # Supply of Ethernet switches & Router cum Firewall is it part of scope. | # The scope of work has been clearly defined for each substation in TS and the same is to be followed. |
|  | # Jharsuguda, Implementation of SAS Upgradation. Volume II, Part 1 of 5, Section – Project, Rev. 00, Clause:4.5.2, Page 13, 14 of 22 |  | # Following details are required : # 1. IED details of Jharsuguda which has to be integrated to SAS. # 2. Overall Panel lay out of Jharsuguda s/s. # 3. SLD of Jharsuguda s/s | # IED details are available in Tender documents. The bidder is advised to visit site and acquaint itself with the site conditions |
|  | # Jharsuguda, Implementation of SAS Upgradation. Volume II, Part 1 of 5, Section – Project, Rev. 00, Clause:4.5.2, Page 13, 14 of 22 |  | # For implementation what would be shut down time provided for Implentation of Upgrdation activity. | # Shall be finalized during execution. However all efforts shall be made to minimize the outage. |
|  | # Jharsuguda, Implementation of SAS Upgradation. Volume II, Part 1 of 5, Section – Project, Rev. 00, Clause:4.5.2, Page 13, 14 of 22 |  | # Integration of IEC61850 devices are : # 1. Existing RTU & Aux BCU # Please confirm | # The scope of work has been clearly defined for each substation in TS and the same is to be followed. |
|  | # Jharsuguda, Implementation of SAS Upgradation. Volume II, Part 1 of 5, Section – Project, Rev. 00, Clause:4.5.2, Page 13, 14 of 22 |  | # Supply of furniture is it part of the scope | # Supply of furniture is not envisaged under present scope. |
|  | # Jharsuguda, Implementation of SAS Upgradation. Volume II, Part 1 of 5, Section – Project, Rev. 00, Clause:4.5.2, Page 13, 14 of 22 |  | # Extension of Power supply from existing ACDB & DCDB in Control room for Powering of supplied device, is it part of scope. | # It is included as per TS |
|  | # Jharsuguda, Implementation of SAS Upgradation. Volume II, Part 1 of 5, Section – Project, Rev. 00, Clause:4.5.2, Page 13, 14 of 22 |  | # Supply of Network panel with ethernet switches is part of scope. | # New panel is acceptable subject to no installation constraints. Same shall be finalized during detailed Engineering. |
|  | # Angul, Bolangir, Keonjhar, Pandiabili, Implementation of SAS Upgradation. Volume II, Part 1 of 5, Section – Project, Rev. 00, Clause:4.5.3, Page 15, 16 of 22 |  | # Will Power Grid Provide IEC61850 configuration file (SCD file of s/s or CID files for all devices to be integrated on IEC61850) during project execution. | # Requisite details shall be provided during detailed engineering. However for any modification required, the bidder has to tie up with respective OEM. |
|  | # Angul, Bolangir, Keonjhar, Pandiabili, Implementation of SAS Upgradation. Volume II, Part 1 of 5, Section – Project, Rev. 00, Clause:4.5.3, Page 15, 16 of 22 |  | # Supply of Ethernet switches & Router cum Firewall is it part of scope. | # The scope of work has been clearly defined for each substation in TS and the same is to be followed. |
|  | # Angul, Bolangir, Keonjhar, Pandiabili, Implementation of SAS Upgradation. Volume II, Part 1 of 5, Section – Project, Rev. 00, Clause:4.5.3, Page 15, 16 of 22 |  | # Following details are required : # 1. IED details ofAngul, Bolangir, Keonjhar, Pandiabili which has to be integrated to SAS. # 2. Overall Panel lay out of Angul, Bolangir, Keonjhar, Pandiabili s/s. # 3. SLD of Angul, Bolangir, Keonjhar, Pandiabili s/s | # IED details are available in Tender documents. The bidder is advised to visit site and acquaint itself with the site conditions |
|  | # Angul, Bolangir, Keonjhar, Pandiabili, Implementation of SAS Upgradation. Volume II, Part 1 of 5, Section – Project, Rev. 00, Clause:4.5.3, Page 15, 16 of 22 |  | # For implementation what would be shut down time provided for Implentation of Upgrdation activity. | # Shall be finalized during execution. However all efforts shall be made to minimize the outage. |
|  | # Angul, Bolangir, Keonjhar, Pandiabili, Implementation of SAS Upgradation. Volume II, Part 1 of 5, Section – Project, Rev. 00, Clause:4.5.3, Page 15, 16 of 22 |  | # Integration of IEC61850 devices are : # 1. Existing RTU & Aux BCU # Please confirm | # The scope of work has been clearly defined for each substation in TS and the same is to be followed. |
|  | # Angul, Bolangir, Keonjhar, Pandiabili, Implementation of SAS Upgradation. Volume II, Part 1 of 5, Section – Project, Rev. 00, Clause:4.5.3, Page 15, 16 of 22 |  | # Supply of furniture is it part of the scope | # Supply of furniture is not envisaged under present scope. |
|  | # Angul, Bolangir, Keonjhar, Pandiabili, Implementation of SAS Upgradation. Volume II, Part 1 of 5, Section – Project, Rev. 00, Clause:4.5.3, Page 15, 16 of 22 |  | # Extension of Power supply from existing ACDB & DCDB in Control room for Powering of supplied device, is it part of scope. | # It is included as per TS |
|  | # Angul, Bolangir, Keonjhar, Pandiabili, Implementation of SAS Upgradation. Volume II, Part 1 of 5, Section – Project, Rev. 00, Clause:4.5.3, Page 15, 16 of 22 |  | # Supply of Network panel with ethernet switches is part of scope. | # New panel is acceptable subject to no installation constraints. Same shall be finalized during detailed Engineering. |
|  | # Jeypore, Baripada, Baripada, Rourkela, Rengali, Supply of RTU Panels replacing existing RTU. Volume II, Part 1 of 5, Section – Project, Rev. 00, Clause:4.6, Page 16 of 22 |  | # Scope is : # 1. Dismnatling of old RTU Panel (if available). # 2. Supply of new RTU Panel (Replacement of any Field control wiring to RTU Panel is not in scope). # 3. OLTC & MFT Tranducer. # Please confirm | # Bidder to comply the Technical Specification. |
|  | # Jeypore, Baripada, Baripada, Rourkela, Rengali, Supply of RTU Panels replacing existing RTU. Volume II, Part 1 of 5, Section – Project, Rev. 00, Clause:4.6, Page 16 of 22 |  | # For supplying RTU Panels in line with RTU Specification following details are required: # 1. No. of DI/DO/AI/AO for Biharsharif, Jamshedpur, Purnea, Sasram & Muzaffarpur ss # 2. No. of OLTC Transducer & MFT Transducer for Biharsharif, Jamshedpur, Purnea, Sasram & Muzaffarpur ss | # This shall be finalized during the survey and detailed engineering. |
|  | # Jeypore, Baripada, Baripada, Rourkela, Rengali, Supply of RTU Panels replacing existing RTU. Volume II, Part 1 of 5, Section – Project, Rev. 00, Clause:4.6, Page 16 of 22 |  | # Specfication calls for RTU with 6 Ethernet ports on IEC 60870-5-104, if requsite ports are not available is it acceptable if unmanaged switch is supplied to meet the requirement. | # Bidder to comply the Technical Specification. |
|  | Volume-III; Bid Form and Price Schedules (Doc. Code No. DC-3032-15629, June 2020) |  |  |  |
|  | # Volume-III of the Bidding Documents | 08_Attachment-23-Authorization Certificate issued by Domestic Manufacturer | In the word file ‘Attachment 21’ is mentioned in the header however name of file mentions ‘Attachment -23’. It seems to be a typing error in the header of file, we understand that it is ‘Attachment-23’ as mentioned in the name of file. Please confirm. | Please refer Amendment-03 of the Bidding Documents. |
|  | # Volume-III of the Bidding Documents | 09_Attachment-24-Affidavit for Self Certification-Iron & Steel | In the word file ‘Attachment 22’ is mentioned in the header however name of file mentions ‘Attachment -24’. It seems to be a typing error in the header of file, we understand that it is ‘Attachment-24’ as mentioned in the name of file. Please confirm. | Please refer Amendment-03 of the Bidding Documents. |
|  | # Volume-III of the Bidding Documents | 10_Attachment-25_E-RA Compliance | In the word file ‘Attachment 23’ is mentioned in the header however name of file mentions ‘Attachment -25’. It seems to be a typing error in the header of file, we understand that it is ‘Attachment-25’ as mentioned in the name of file. Please confirm. | Please refer Amendment-03 of the Bidding Documents. |
|  | # Volume-III of the Bidding Documents | 11_Attachment-26_Declaration regarding events encountered pursuant to ITB Clause 2.1 | In the word file ‘Attachment 25’ is mentioned in the header however name of file mentions ‘Attachment -26’. It seems to be a typing error in the header of file, we understand that it is ‘Attachment-26’ as mentioned in the name of file. Please confirm. | Please refer Amendment-03 of the Bidding Documents. |
|  | # '02_Second Envelope Bid Vol-III_Pkg-Y' Bid Price Schedule: # Instructions sheet | # Sch-4a (Training Charges) : Not applicable, hence no cell is required to be filled up. | # As per the instructions sheet of price bid schedule, Schedule 4a (Training charges) and Schedule 4b (maintenance charges during and after defect liability period) are mentioned as NOT APPLICABLE and there is NO NEED to fill Sch 4a and Sch 4b by the bidder. We understand Training and AMC as per these schedules are NOT in the scope of this tender. Please confirm | # Please refer Amendment-03 of the Bidding Documents. |
|  | # '02_Second Envelope Bid Vol-III_Pkg-Y' Bid Price Schedule: # Instructions sheet & RTU Technical Specification_Rev02 : 1.32 | # Duration of training shall be 25 mandays. | # As per Price Bid Schedule Instructions - Sch 4a is not applicable. So we understand any kind of training is not in scope of this tender. Please confirm. | # Training is in the scope of tender. # Please refer Amendment-03 of the Bidding Documents. |
|  | # '02_Second Envelope Bid Vol-III_Pkg-Y' Bid Price Schedule: # Instructions sheet & RTU Technical Specification_Rev02 : 1.32 | # Duration of training shall be 25 mandays. | # As per Price Bid Schedule Instructions - Sch 4a is not applicable. So we understand any kind of training is not in scope of this tender. Please confirm. | # Training is in the scope of tender. # Please refer Amendment-03 of the Bidding Documents. |
|  | # '02_Second Envelope Bid Vol-III_Pkg-Y' Bid Price Schedule: # Instructions sheet & RTU Technical Specification_Rev02 : 1.33 | # Sch-4b (Maintenance Charges during and after Defect Liability Period): Not applicable, hence no cell is required to be filled up. | # As per Price Bid Schedule Instructions - Sch 4b is not applicable. So we understand any kind of AMC/Maintenance is not in scope of this tender. Please confirm. | # AMC/ Maintenance is in the scope of tender. # Please refer Amendment-03 of the Bidding Documents. |