| Clarification No. – 03 (Technical) dated 26/05/2023 to the Bidding Documents of 765kV AIS Substation Extn. Package SS-86 for (i) Extension of 765/400/220 kV Fatehgarh-III Substation including 2X125 MVAR, 420 kV Bus Reactors associated with “Transmission system for evacuation of power from REZ in Rajasthan (20GW) under Phase-III Part E1” and (ii) 1 set of Bus Sectionalizer at 400kV level of 765/400/220kV Fatehgarh-III PS (Section-2). Spec. No.: CC/NT/W-AIS/DOM/A00/23/01627 |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| S. No. | Volume/Section Clause No. |  | Description | Query | POWERGRID's Reply |
|  | Section-Project: clause 2.2.1.1.g), 2.2.2.1 c), Remote end works |  |  | As per referred clause in section project, we presume that no work is envisaged at remote end (RLDC/ Backup RLDC /RTAMC/ NTAMC / Backup NTAMC/RTAMC) under the present scope. Please confirm whether bidder understanding is inline with specification requirement. | Confirmed, However, refer clause 2.2.1.1.g) and 2.2.2.1.c) for better understanding. |
|  | Section-Project: clause 2.2.1.1.p), DSLP |  |  | As per referred clause, it is mentioned as "The lightning protection (DSLP) for complete switchyard is to be provided by the contractor. The contractor shall design the lightning protection by utilizing the structures being provided under present scope". Hence, we presume that the DSLP coverage shall be provided for bays under present scope of work only. Please confirm. | Confirmed. |
|  | Section-Project: clause 2.2.1.1 (c) |  |  | We understand our scope is limited to integration with existing system and any hardware/software are not required for upexisting system upgradation. We understand existing system is capable enough to cater present bays without any Hardware & Software upgradation. Kindly confirm. | Bidder to quote as per the requirement of Substation Automation specified at clause no. 2.2.1.1.g) and 2.2.2.1.c) of Section Project. |
|  | Annexure-III_Specific Requirement_Rev 07 with Annexures, Q.2 to Q.5 and Q.9 |  |  | We understand our scope is limited to integration of present bays to exisiting SAS, hence supply of following equipments are not in our scope of supply. 1.Gateways 2. Ethenet Switch for NTMAC Sub-systems conncetion 3. NGFW 4. Routers 5. Disturbance Recorder Kindly confirm. | Supply of Gateways, Ethernet Switch and Router for NTMAC Sub-systems connection, Next generation fire wall and Engineering PC is not envisaged under present scope. Refer clause no. 2.2.1.1.g) and 2.2.2.1.c) of Section Project for scope under Substation Automation |
|  | Section-Project : clause 2.2.1.1 t PMU |  |  | As per referred clause, it is mentioned as "The Scope of the procurement of PMU shall include planning, designing, engineering, supply, transportation, insurance, delivery at site, unloading handling, storage, installation, termination, testing and demonstration for acceptance, commissioning and documentation for PMU as per BPS and these PMU shall support IEEE C 37.118 protocols. These PMUs shall be integrated with Phasor data Concentrator (PDC) at Northern Regional Load Dispatch Centre." However, we understand the same as follows: 1)PMU integration with PDC at Northern Regional Load Dispatch Centre end is not the present scope of bidder. 2)Technical support shall be extended for seamless integration with PDC at local end. In this regard, Please specify the make & model of Phasor Data concentrator at Northern Regional Load Dispatch Centre. Further, we are not envisaging any hardware upgradation/new supply/Software upgradation at PDC. Please confirm. | Yes The integration work at RLDC end will NOT be under the scope of the Bidder. However, the Bidder shall extend technical support at local end for seamless integration of PMU with PDC at remote end. The existing PDC system at RLDC end was supplied by M/s GE. Yes, NO scope of Supply/Service at PDC end at RLDC. |
|  | Section-Project : clause 2.2.1.1 s) (vii) NMS |  |  | We understand that NMS integration is limited to Fatehgarh-III substation end configuration only. Any work at central NMS server is not in the present scope of bidder. Kindly confirm. | At SS End : Bidder has to provide Telecom Equipment which can be integrated in the existing NMS. Configuration work for necessary integration with existing NMS in supplied FOTE shall be in scope of Bidder At Central NMS Server End: Existing NMS Provider/Support team will do the necessary integration/Configuration in existing NMS, However, all necessary support to integrate new Telecom equipment in the existing NMS shall be ensured by the Bidder. |
|  | Section-Project : clause 2.2.1.1 p) (iv) , Existing Communication equipment details |  |  | As per referred clause, Integration with the existing communication system shall be in the scope of bidder. In this regards, please provide the following details a) Make and model of FOTE equipment b) Transmission capacity (STM-1/SM-4/STM-16) c) Number of spare teleprotection interface cards/data interface cards/speech interface cards d) Existing communication drawing | Bidder to quote as per BPS. Details shall be provided to the successful bidder during detailed engineering in the event of award. |
|  | ACDB and DCDB extension |  |  | As per section project and BPS, we presume that sufficient feeders are already available in the existing ACDB and DCDB for the present of works. Bidder to consider the cable along with terminations only from existing boards to respective panels/equipments under present scope of works. Please confirm. | Confirmed. |
|  | Fatehgarh-III substation - Existing Drawings |  |  | Please provide the following drawings Fatehgarh-III substation existing Substation. i) Existing control building layout ii) Visual monitoring system (VMS) layout iii) Lightning protection layout. iv) Existing Outdoor Illumination Layout | Details shall be provided to the successful bidder during detailed engineering in the event of award. |
|  | Line lengths |  |  | Please furnish the line lengths for the following lines in order to choose the appropriate protection & communication interfaces: a) 765kV line from Fatehgarh-III to Beawar | Bidder to quote as per BPS. |
|  | Busbar Protection for 765kV,400kV and 220kV |  |  | As the 765kV, 400kV and 220kV is existing,Please provide the details of 765kV,400kV and 220kV bus bar protection system. a) Make & Model number b) Centralized or Decentralized type? c) If decentralized type, whether Bay units are already available for the bays proposed under this package. | Bidder to quote as per the requirement of Peripheral units for Bus Bar Protection scheme as specified at clause no. 2.2.1.1-f) and 2.2.2.1.b) of Section Project. Further, Make and model of existing bus bar for 400 Section-I is GE make P741 de-centralized Bus Bar Protection. Peripheral units of Decentralized Bus bar protection for 400kV Bus Sectionalizer-1 under present scope is available at site. Shifting of these peripheral units from existing panels to present bays panels including necessary modifications, wiring and commissioning for completion of the bus bar protection scheme is deemed to be included under present scope. Bus Bar Protection for the 400kV Section-II and Section-III is new. |
|  | Battery and battery charger |  |  | We are not considering any 220V and 48V Battery and battery charger for present scope of works. We presume that existing battery and battery chargers are already sized by considering future extension of bays which were under present scope of works. Please confirm. | Confirmed. |
|  | Protection relays at remote end |  |  | We propose the Main protection as Distance protection for all 400kV & 220kV lines. a) If differential protection need to be considered, please clarify the scope of remote end differential relays (supplied as loose)?. b) If remote end differential relays are already available, please confirm the make & model number. | Bidders are to quote as per Bidding Document. |
|  | Creepage distance |  |  | As per section project, it is mentioned as "Minimum specified creepage distance for insulator string/ longrod insulators/ outdoor bushings shall be 31 mm/kV". We presume that except mentioned insulator string/longrod insulators/outdoor bushings ,all other outdoor equipment such as CB,CVT,LA,CT & BPI etc. shall have 25mm/kV creepage. Please confirm whether bidder understanding is correct. | Creepage for all equipment shall be 25mm/kV. However, for insulator string/ long rod insulators/ outdoor bushings, refer clause 9.4 of Section-Project. |
|  | Order of Precedence |  |  | Please describe the order of precedence of price schedule (BPS), technical specification and section project. | In case of mismatch of details in BPS & TS, details mentioned in BPS shall prevail. However if adequate details are not specified in BPS, then BPS Item shall be read in conjunction with TS. As per clause 7.0 of Section Project “In case of any contradiction between Section Project & other sections of Technical specification, Requirement of Section Project shall prevail. In case of any discrepancy between Section-GTR and individual sections for various equipments, requirement of individual equipment section shall prevail.” |
|  | General |  | Soil Investigation Report | Kindly request you to provide soil investigation reports for proposed extension for tender working. | Details shall be provided to the successful bidder during detailed engineering in the event of award. |
|  | General- Layout / Drawing |  | Plan & Section | Request to please provide Typ. Plan & Section of 765/400KV Auto Transformer Neutral & Delta formation. | Details shall be provided to the successful bidder during detailed engineering in the event of award. |
|  | BPS; Sr. 161&162 Tower and gantry Structure BPS; Sr. 110 to 128 |  | Fabrication, galvanising and supply of Lattice Structures (MS Steel),to be designed during detailed engineering, for towers, beams and equipment support structure including pack plates / packwashers andgusset plates excluding fasteners and foundation bolts | We understand that these line items are applicable for Tower and Gantry Structures only, Not for Equipment structures. As equipment structrues line items are mentioned separately in Sr no. 110 to 128. Kindly confirm. | BPS serial no. quoted to be reconfirmed. However, refer BPS and clause no. 2.2.1.1.r and 2.2.2.1.h of Section- Project for better understanding. |