| S.No | Clause No | Existing Clause | Amended Clause |  |
| --- | --- | --- | --- | --- |
|  | GCC 22.8.1 in SCC, Section-V, Vol-I of Bidding Document | Replacing Sub-Clause GCC 22.8.1 with the following: At the end of the Defect Liability Period, the Contractor's Liability ceases except for latent defects. The Contractor's liability for latent defects warranty shall be limited to period of ten (10) years from the end of Defect Liability Period. Latent defects are such defects for which it is established by the Employer that the defect was discovered/noticed after the date of expiration of the Defect Liability Period.................... | Replacing Sub-Clause GCC 22.8.1 with the following: At the end of the Defect Liability Period, the Contractor's Liability ceases except for latent defects. The Contractor's liability for latent defects warranty shall be limited to period of five (5) years from the end of Defect Liability Period. Latent defects are such defects for which it is established by the Employer that the defect was discovered/noticed after the date of expiration of the Defect Liability Period.................... |  |
|  | Bidding Documents, Vol-II | Chapter-1 Updated | “Chapter-1 Updated” stands deleted |  |
|  | Chapter-1 1.2 a) | The scope of work for… xiv. Two (02) numbers 85 inches, Ultra HD LED… | xi. AC Control and protection… (ADD at the end) 6. Complete upgradation and digitalisation of south side AC lines (Ramagundam 1 & 2 ) along with respective line reactors protection and their integration in HVDC SCADA (ADD at the end) xv. Replacement of all control and power cables of 12 no (6 west side & 6 south side) converter transformers |  |
|  | Chapter-1 1.3.3.4 Type Testing | As per CEA (Central Electricity authority) the Guidelines for validity period of type test(s) conducted on Major Electrical equipments in Power Transmission system is available in the CEA website at the link http://cea.nic.in/reports/ others / ps / psetd / Approved_Type%20test%20validity%20guidelines. | As per CEA (Central Electricity authority) the Guidelines for validity period of type test(s) conducted on Major Electrical equipments in Power Transmission system is available in the CEA website at the link: https://cea.nic.in/wp- content/uploads/notification/2021/09/Amended_CEA_Guideline_of_Type_Test_Validity_17092021.pdf |  |
|  | Chapter-1 1.3.4 Civil Works | ………………………….. (iii) Valve Cooling UPS battery building as per Annexure Battery Room ………….. | ………………………….. (iii) Valve Cooling UPS battery building as per Annexure Battery Room Finishing schedule shall be as per Annexure-I ……………………………. |  |
|  | Chapter-1 1.4.5 PERFORMANCE GUARANTEES | ………………………. In addition, the following Performance Guarantees in respect of equipment being replaced/installed under present scope shall be provided by the Contractor, as - Energy Availability - Reliability - Station power rating - Thyristor failure rate - Relay module/C & P module/Component failure rate - Shutdown Duration …………………………. | ………………………. In addition, the following Performance Guarantees in respect of equipment being replaced/installed under present scope shall be provided by the Contractor, as - Energy Availability - Reliability - Station power rating - Thyristor failure rate - Relay module / C&P module / Component failure rate - Shutdown Duration - Station Efficiency (Station Loss) …………………………. |  |
|  | Chapter-1 1.8.1 Technical Requirement of HVDC Equipment | 1.8.1.1 The following HVDC equipment shall be offered from a regular manufacturer(s) who have been manufacturing such equipment(s) for HVDC system for the last (5) five years or more as on the originally scheduled date of the bid opening and should have been in operation for at least two (2) years as on the originally scheduled date for the dead line for submission of bid. | 1.8.1.1 The following HVDC equipment shall be offered from a regular manufacturer(s) who have been manufacturing such equipment(s) for HVDC system for the last (5) five years or more as on the originally scheduled last date of bid submission (soft copy) specified in Annexure-A(BDS) and should have been in operation for at least two (2) years as on the originally scheduled last date of bid submission (soft copy specified in Annexure-A(BDS). |  |
|  | Chapter-1 1.8.1 Technical Requirement of HVDC Equipment | ……………………. The Indian manufacturer should have an association/collaboration with the principal manufacturer who meets the requirements of clause 3.1 of QR specified in Section- EQC, Part- I of the Bidding Documents. ………………………. ……………………… The Indian manufacturer should have an association / collaboration with the parent company who meets the requirements of clause 3.1 of QR specified in Section-EQC, Part- I of the Bidding Documents. …………………… | ……………………. The Indian manufacturer should have an association/collaboration with the principal / parent / Group Company who meets the requirements of clause 3.1 of QR specified in Annexure-A (BDS), Vol- I of the Bidding Documents. ………………………. ……………………… The Indian manufacturer should have an association / collaboration with the parent /principal/ group company who meets the requirements of clause 3.1 of QR specified in Annexure-A (BDS, Vol- I of the Bidding Documents. …………………… |  |
|  | Chapter-1 1.9 and 1.10 | 1.9 In case, the bidder is a foreign entity… 1.10 Requirement of ‘Associate(s)’… | Deleted |  |
|  | Chapter-1 Annexure Outage Schedule | Annexure Outage Schedule | Annexure Outage Schedule_Rev 01 |  |
|  | Chapter-1 Annexure Store Area | Annexure Store Area | Annexure Store Area rev01 |  |
|  | Chapter-1 1.14 Requirement of Cyber Security | Cyber Security requirement is enclosed at Annexure-Cyber Security. | Cyber Security requirement is enclosed at Annexure-Cyber Security. Detailed Cyber Security Requirements, FAT Checklist & SAT Checklist of Control and Protection IEDs & other components are attached as Annexure-S12 (Annexure-II)- Cyber Security Requirements_ R0, Annexure-S13 (Annexure-III) -- FAT_Checklist_R0 & Annexure-S14 (Annexure-IV) --SAT_Checklist_R0 respectively |  |
|  | Chapter -4 4.8.1 | The asynchronous data interface is required for communication between Remote Terminal Units (RTU) to be located at Chandrapur to Southern Regional Load Dispatch Centre (SRLDC) | The asynchronous data interface is required for communication between Remote Terminal Units (RTU) to be located at Chandrapur to Southern Regional Load Dispatch Centre (SRLDC), WRLDC (Western region load despatch centre and NLDC (National load despatch centre) |  |
|  | Chapter -4 4.11.7 AUDIBLE NOISE: | ……………… Mechanical Equipment Indoor areas having long term access (measured at 2 meter distance) : 75 dBA Equipment in outdoor areas (measured at 15 meter distance) : 75dBA ……………… | ……………… Mechanical Equipment Indoor areas having long term access (measured at 2 meter distance) : 80 dBA Equipment in outdoor areas (measured at 15 meter distance) : 75dBA ……………… |  |
|  | Chapter-8 8.9.7 PRE-ENGINEERED STORE BUILDING | ……….. Size : About 18mx80M (without any internal columns) …………….. | ……….. Size : About 20Mx90M (without any internal columns) …………….. |  |
|  |  | # GUARANTEES The Guaranteed parameters as stated below to be established by the contractor for Block 1 with 500 MW in parallel operation with Block 2 with 500 MW are :- -Station Power rating - Availability - Reliability - Station Efficiency (Station Loss) -Thyristor failure Rate - Guaranteed failure Rate of Relay module/C&P module /components | # GUARANTEES The Guaranteed parameters as stated below to be established by the contractor for Block 1 with 500 MW in parallel operation with Block 2 with 500 MW are :- -Station Power rating - Availability - Reliability - Station Efficiency (Station Loss) -Thyristor failure Rate -Guaranteed failure Rate of Relay module/C&P module /components - Shutdown duration / Outage schedule (Refer Chapter 1 clause 1.11) |  |
|  | Chapter-11 11.4.1.2 Capacity Terms | …………………. .3 OUTAGE DERATING FACTOR (ODF) The ratio of outage capacity (Po) to maximum continuous capacity (Pm). 11.4.1.3 ODF = Po / PmOutage Duration Terms. ……………………. | …………………. .3 OUTAGE DERATING FACTOR (ODF) The ratio of outage capacity (Po) to maximum continuous capacity (Pm). ODF = Po / Pm 11.4.1.3 Outage Duration Terms. ……………………. |  |
|  | Chapter-11 11.4.1.4 Capacity Terms | .1 PERIOD HOURS (PH) The number of hours in the reporting period. In a full year the Period Hours are 8760 h (8784 h for a leap year). If the equipment is commissioned part way through a year the period hours shall be proportionately less than 8760 h. (This shall not be applicable for verification of guarantees). …………………… | .1 PERIOD HOURS (PH) The number of hours in the reporting period. In a half- year the Period Hours are 4380 h (4392 h for a leap year). If the equipment is commissioned part way through a half-year, the period hours shall be proportionately less than 4380 h. (This shall not be applicable for verification of guarantees). …………………… |  |
|  | Chapter-11 11.4.1.5 Availability and Reliability Terms | ……………………… .4 RELIABILITY is expressed in terms of the number of forced outages of curtailment occurrences of Block per unit of time, usually one year. ……………………….. | ……………………… .4 RELIABILITY is expressed in terms of the number of forced outages of curtailment occurrences of Block per unit of time, in this project this shall be a period of six consecutive months. ……………………….. |  |
|  | Chaspter-11 11.5.2 GUARANTEES REQUIRED | ………………….. The operation of the 2x500 MW block -1 & 2 shall be monitored during the guarantee period of minimum 12 months by a data base software developed by the Contractor incorporating details as specified under clause 11.4 to determine whether it meets the guarantees. …………………………… | ……………………… The operation of the 2x500 MW block-1 & 2 shall be monitored during the guarantee period on per block basis for a minimum duration of two consecutive periods of six months (12 months in total) each by a data base software developed by the Contractor incorporating details as specified under clause 11.4 to determine whether it meets the guarantees. …………………………………………. |  |
|  | Chapter-11 11.6 DESIGN PRINCIPLES | ………………….. The Contractor shall design the control & protection equipment, to cause no more than 5 transient disturbances (with a duration exceeding 20 ms) per block per six months. Transient disturbances in connection with events resulting in forced outages shall be excluded from the above. When more than one transient disturbance occurs within a time period of (max.) 10 sec in connection with the same failure or mis-operation, this shall be counted as single transient disturbance. ………………… | ………………….. The Contractor shall design the control & protection equipment, to cause no more than 5 transient disturbances (with a duration exceeding 20 ms) per block per six months. Transient disturbances in connection with events resulting in forced outages shall be excluded from the above. When more than one transient disturbance occurs within a time period of (max.) 10 sec in connection with the same failure or mis-operation, this shall be counted as single transient disturbance. ………………… |  |
|  | Chapter-11 11.7 AVAILABILITY AND RELIABILITY CALCULATIONS 11.7.1 GENERAL | ……………. Definitions of availability and outage state conditions are given in Clause 11.4.1. The period basis for availability and reliability calculations shall be 12 consecutive months (one year). The period over which the guarantees are to be in effect shall be twelve (12) months (i.e. one year), or any valid extension thereof, commencing six months after successful completion of trial operation of each 500 MW block …………………….. | ……………………… Definitions of availability and outage state conditions are given in Clause 11.4.1. The period basis for availability and reliability calculations shall be 6 consecutive months (half-year). The period over which the guarantees are to be in effect shall be two consecutive periods of six (06) months (i.e. two half- years), or any valid extension thereof, commencing six months after successful completion of trial operation of each 500 MW block .. ……………………………………… |  |
|  | Chapter-11 11.8 AVAILABILITY REQUIREMENT | 11.8.1 ………………………. Also, subject to the terms and conditions specified, the availability per year, considering forced outages, shall be equal to or exceed the guaranteed value. ………………… | 11.8.1 ………………………. Also, subject to the terms and conditions specified, the availability per six months, considering forced outages, shall be equal to or exceed the guaranteed value. ………………… |  |
|  | Chapter-11 11.8.2 FULFILLMENT OF AVAILABILITY GUARANTEE | (a) If the annual energy availability, averaged over the 12 months (one year) guarantee period, proves to be below the guaranteed value, the guarantee period shall be extended by six months. If at the end of this six months, the one year average energy availability, disregarding the half year (any 6 consecutive months) with the lowest availability is equal to or higher than the guaranteed value, then the availability guarantee shall be considered as fulfilled. | (a) If the semi-annual energy availability, averaged over the 6 months during the two consecutive periods of 6 months each guarantee period, proves to be below the guaranteed value, the guarantee period shall be extended by six months. If at the end of this six months, the average energy availability over 6 months in any two out of three periods of six months each, disregarding the half year (any 6 consecutive months) with the lowest availability is equal to or higher than the guaranteed value, then the availability guarantee shall be considered as fulfilled. |  |
|  | Chapter-11 11.8.2 FULFILLMENT OF AVAILABILITY GUARANTEE | (b) If the annual energy availability averaged over the best one year period is still below the guaranteed value, the Contractor shall correct all design deficiencies and equipment defects at no cost to the Employer. | (b)If the semi-annual energy availability averaged over the best two periods of six months each is still below the guaranteed value, the Contractor shall correct all design deficiencies and equipment defects at no cost to the Employer. |  |
|  | 11.8.2 FULFILLMENT OF AVAILABILITY GUARANTEE | (c) After correction of such deficiencies and defects, if the annual energy availability averaged over a further half year period (excluding the previous one and half year period and the period for correcting such deficiencies) is still below the guaranteed value, liquidated damages calculated as given below shall be paid by the Contractor to the Employer. …………………. | (c) After correction of such deficiencies and defects, if the semi-annual energy availability averaged over a further half year period (excluding the previous one and half year period and the period for correcting such deficiencies) is still below the guaranteed value, liquidated damages calculated as given below shall be paid by the Contractor to the Employer." |  |
|  | Chapter-11 11.9.2 FULFILLMENT OF RELIABILITY GUARANTEE | (a) If the number of occurrences/six monthly (EOF/TD) averaged over the 12 months (one year) guarantee period exceeds the guaranteed value, the guarantee period shall be extended by six months. If, at the end of the extended period the one year average number of occurrences/6 months, disregarding any six consecutive months with the highest number of occurrences/6 months, is equal to or lower than the guaranteed number of occurrences/6 months then the reliability guarantee shall be considered as fulfilled. | (a) "If the number of occurrences/six monthly (EOF) during the two consecutive guarantee periods of 6 months each exceeds the guaranteed value, the guarantee period shall be extended by six months. If, at the end of the extended period the average number of occurrences/6 months in any two out of three periods of six months each, disregarding any six consecutive months with the highest number of occurrences/6 months, is equal to or lower than the guaranteed number of occurrences/6 months then the reliability guarantee shall be considered as fulfilled. |  |
|  | Chapter-11 11.12 GUARANTEED FAILURE RATE OF THYRISTORS | .3 The thyristor failure rate shall be monitored over a period of 12 months starting at the end of six months following trial operation of the HVDC system. If the average failure rate of thyristors, over a period of these 12 months proves to be within the guaranteed value the guarantee shall be considered as fulfilled otherwise the guarantee period shall be extended by six (06) months. If the average failure rate of thyristors at the end of the extended period, the one year average number of occurrences/6 months, disregarding any six consecutive months with the highest thyristor failure rate is equal to or lower than the guaranteed value then the thyristor failure rate guarantee is considered to be fulfilled.. | .3 The thyristor failure rate shall be monitored over two consecutive periods of 6 months each, starting at the end of six months following trial operation of the HVDC system. If the average failure rate of thyristors, over a period of these 6 months in both consecutive periods proves to be within the guaranteed value the guarantee shall be considered as fulfilled otherwise the guarantee period shall be extended by six (06) months. If the average failure rate of thyristors (averaged over six months per period) at the end of the extended period, during any two out of three periods of the six months each average, disregarding any period of six consecutive months with the highest thyristor failure rate is equal to or lower than the guaranteed value then the thyristor failure rate guarantee is considered to be fulfilled. |  |
|  | Chapter-11 11.13 GUARANTEED FAILURE RATE OF RELAY MODULE/C&P MODULE / COMPONENT | ……………………….. The relay module / C&P module/ Component failure rate shall be monitored on per block basis over a period of six months starting at the end of six months after trial operation of HVDC system. If the failure rate of each type of relay module/C&P module/component averaged during these twelve months proves to be within the specified value, the guarantee shall be considered as fulfilled otherwise the guaranteed period shall be extended by six months. ………….. | ………………………….. The relay module / C&P module/ Component failure rate shall be monitored on per block basis over two consecutive periods of six months starting at the end of six months after trial operation of HVDC system. If the failure rate of each type of relay module/C&P module/component averaged during these two consecutive periods of six months each proves to be within the specified value, the guarantee shall be considered as fulfilled otherwise the guaranteed period shall be extended by six months. ………….. |  |
|  | Chapter-11 of Technical specification 11.9.2 FULFILLMENT OF RELIABILITY GUARANTEE | As stated above, the Employer shall monitor the operation of the HVDC system during the guarantee period for each block individually. An annual appraisal of reliability performance shall be jointly made by the Employer and the Contractor to determine whether correction of design deficiencies, if any, is warranted. Evaluation of EOF and transient disturbance shall be made separately. With respect to the guaranteed reliability values for curtailment in HVDC system capacity, the following shall apply: (a) If the number of occurrences/six monthly (EOF/TD) averaged over the 12 months (one year) guarantee period exceeds the guaranteed value, the guarantee period shall be extended by six months. If, at the end of the extended period the one year average number of occurrences/6 months, disregarding any six consecutive months with the highest number of occurrences/6 months, is equal to or lower than the guaranteed number of occurrences/6 months then the reliability guarantee shall be considered as fulfilled. (b) If the number of occurrences/6 months averaged over the one year period exceeds the guaranteed value, the Contractor shall correct all design deficiencies and equipment defects at no cost to the Employer. (c) After correction of such deficiencies and defects, if the number of occurrences/6 months over a further half year period (excluding the previous one and half year period and the period for correcting such deficiencies) is still above the guaranteed value, liquidated damages calculated as per the formula below shall be paid by the Contractor to the Employer: = Rs. 1 Million for each EOF or part thereof above the guaranteed value. = Rs. 0.5 Million for each transient disturbance or part thereof above the guaranteed value | As stated above, the Employer shall monitor the operation of the HVDC system during the guarantee period for each block individually. An annual appraisal of reliability performance shall be jointly made by the Employer and the Contractor to determine whether correction of design deficiencies, if any, is warranted. Evaluation of EOF and transient disturbance shall be made separately. With respect to the guaranteed reliability values for curtailment in HVDC system capacity, the following shall apply: (a) If the number of occurrences/six monthly (EOF/TD) averaged over the 12 months (one year) guarantee period exceeds the guaranteed value, the guarantee period shall be extended by six months. If, at the end of the extended period the one year average number of occurrences/6 months, disregarding any six consecutive months with the highest number of occurrences/6 months, is equal to or lower than the guaranteed number of occurrences/6 months then the reliability guarantee shall be considered as fulfilled. (b) If the number of occurrences/6 months averaged over the one year period exceeds the guaranteed value, the Contractor shall correct all design deficiencies and equipment defects at no cost to the Employer. (c) After correction of such deficiencies and defects, if the number of occurrences/6 months over a further half year period (excluding the previous one and half year period and the period for correcting such deficiencies) is still above the guaranteed value, liquidated damages calculated as per the formula below shall be paid by the Contractor to the Employer: = Rs. 1 Million for each EOF or part thereof above the guaranteed value. = Rs. 0.5 Million for each transient disturbance or part thereof above the guaranteed value |  |
|  | Cl. 3.1 IFB, Section-I, Vol-I of Bidding Document | 3.1 The scope of work covered under the subject package covers the following: - The refurbishment of existing Chandrapur Station includes the refurbishment of one completely operational back to back HVDC station…………………………….. ……………………………. xi) AC Control and protection system for 400 kV Busbar, AC harmonic filter and converter bays and Converter transformer Scope for AC control and protection system for AC Yard is as follows: - Converter transformer. - Replacement of Complete Bus bar protection from High impedance to low impedance for Western side and Southern Side Bus Bars along with Cables from Switchyard to HVDC Control room. - Converter transformers bay and AC filter bays for each Pole on both West and South side. - AC filter sub bank bays for each Pole and each side. - Replacement of High Impedance Interzone protection with low Impedance Interzone protection. Existing C&P cubicles for the above shall be completely dismantled and stored at site. xii) Replacement of 48V, 220V battery Chargers with new 220V and 48V battery chargers (new charger system should have facilities for DC earthing & Monitoring) and integration with existing DCDB. xiii) Suitable covered storage Area as per Annexure store area. Space for storage Area is marked in Annexure store Area, approx. 1800 Sqmeter. Space for Valve cooling coolers are shown in Annexure Valve cooling Area. | 3.1 The scope of work covered under the subject package covers the following: - The refurbishment of existing Chandrapur Station includes the refurbishment of one completely operational back to back HVDC station…………………………….. ……………………………. xi) AC Control and protection system for 400 kV Busbar, AC harmonic filter and converter bays and Converter transformer Scope for AC control and protection system for AC Yard is as follows: - Converter transformer. - Replacement of Complete Bus bar protection from High impedance to low impedance for Western side and Southern Side Bus Bars along with Cables from Switchyard to HVDC Control room. - Converter transformers bay and AC filter bays for each Pole on both West and South side. - AC filter sub bank bays for each Pole and each side. - Replacement of High Impedance Interzone protection with low Impedance Interzone protection. - Complete upgradation and digitalisation of south side AC lines (Ramagundam 1 & 2 ) along with respective line reactors protection and their integration in HVDC SCADA. Existing C&P cubicles for the above shall be completely dismantled and stored at site. xii) Replacement of 48V, 220V battery Chargers with new 220V and 48V battery chargers (new charger system should have facilities for DC earthing & Monitoring) and integration with existing DCDB. xiii) Suitable covered storage Area as per Annexure store area. Space for storage Area is marked in Annexure store Area, approx. 1800 Sqmeter. Space for Valve cooling coolers are shown in Annexure Valve cooling Area. xiv. Two (02) numbers 85 inches , Ultra HD LED television of reputed make and latest technology along with suitable support stand for optimum viewing from control desk, shall be supplied. The above shall be used for monitoring of the DC and AC equipments associated with the converters, complete with status indication devices and measured values. LED display shall include full active display for the complete DC equipments and AC systems of Chandrapur BtB station and essential indications and measured analog values. xv. Replacement of all control and power cables of 12 no (6 west side & 6 south side) converter transformers. |  |
|  | Appendix-1 (Terms and Procedures of Payment), Sample Forms and Procedures, Section-VI | Appendix-1 TERMS AND PROCEDURES OF PAYMENT In accordance with the provisions of GCC Clause 8 (Terms of Payment), the Employer shall pay the Contractor in the following manner and at the following times, on the basis of the Price Breakdown given in the section on price schedules. Payments will be made in the currencies quoted by the Bidder unless otherwise agreed between the parties. The Contractor may make applications for payment in respect of part deliveries as work proceeds. 1. TERMS OF PAYMENT In addition to the Conditions stipulated under GCC Clause 8, the following terms & Conditions will apply. - Supply of Goods Portion: …………………………………… C Progressive Payment …………………………………… C.1 Fifteen percent (15%)^# of the Ex-Works price component … … … … … … … … … …………………. C.2 Fifteen percent (15%)## of the Ex-works price of Main Equipment/Materials … … … … … … … … … … … … … … … …………………………….. 2. PAYMENT PROCEDURES 2.1 Method of Payment … …. …. ….. … …. …. …. 2.2 Bill Tracking System … …. …. ….. … …. …. …. | Appendix-1 TERMS AND PROCEDURES OF PAYMENT In accordance with the provisions of GCC Clause 8 (Terms of Payment), the Employer shall pay the Contractor in the following manner and at the following times, on the basis of the Price Breakdown given in the section on price schedules. Payments will be made in the currencies quoted by the Bidder unless otherwise agreed between the parties. The Contractor may make applications for payment in respect of part deliveries as work proceeds. 1. TERMS OF PAYMENT In addition to the Conditions stipulated under GCC Clause 8, the following terms & Conditions will apply. - Supply of Goods Portion: …………………………………… C Progressive Payment $ …………………………………… C.1 Fifteen percent (15%)^# of the Ex-Works price component … … … … … … … … … …………………. C.2 Fifteen percent (15%)## of the Ex-works price of Main Equipment/Materials … … … … … … … … … … … … … … … $ Percentage of Progressive Payment shall be suitably adjusted in case of unbalanced/ front loaded bid as per the methodology brought-out at sl. No. 2.3 below. … …. …. ….. … …. …. …. 2. PAYMENT PROCEDURES 2.1 Method of Payment … …. …. ….. … …. …. …. 2.2 Bill Tracking System … …. …. ….. … …. …. …. 2.3 PAYMENT PROCEDURES IN CASE OF UNBALANCED / FRONT LOADED BID a. A bid shall be considered front loaded or unbalanced, if the percentage of Services component (Installation, civil works, F&I and Training, if any) to Total Contract Price (Supply component + Services component) quoted by the bidder is less than 16%. b. In the event of award on the bidder who have submitted unbalanced/front loaded bid, the percentage of Progressive payment against Supply of Goods portion (refer sl. No. 1.1 above) shall be deferred by the percentage by which the percentage of the Services price components in the bid less than the percentage specified at 2.3 a above in the bidding documents. No interest shall be payable on the deferred amount. The aforesaid deferred amount shall be paid on pro-rata basis upon completion of installation of the respective item and its certification by the Project Manager. No interest shall be payable on the deferred amount. Price Variation and Quantity variation shall continue to be governed by the unit price quoted by the bidder. |  |
|  | GCC 23.3(b) in SCC, Section-V, Vol-I of Bidding Document | Replace the Sub- Clause GCC 23.3(b) in SCC: pay liquidated damages to the Employer in respect of the failure to meet the Functional Guarantees and Shut down duration/ Outage Schedule as specified at Chapter-11 and Clause 1.11 of Part-1 of Technical Specifications, Vol-II of the Bidding Documents and as per rates given here under: S.N; Parameters for levy of liquidated damages on failure to meet the guarantees; Liquidated Damages. 1.; Station Losses for Block-1 & Block-2 individually - a) No load losses(KW) - b) Equivalent load losses (KW); - No load losses@ INR 0.8 million per KW - Equivalent load losses@ 0.4 million per KW. 2.; System Availability Minimum Energy availability requirement for each Block per half year; INR 30 Million for each 0.1% or part thereof for the shortfall below 99.8% down to 98%. 3.; System Reliability a) Equivalent Outage Frequency (EOF) for each Block per half year b) Transient Disturbances per Block per half year; - INR 1 Million for each EOF or part thereof above the guaranteed value - INR 0.5 Million for each Transient Disturbance or part thereof above the guaranteed value. 4.; Station Power Rating Guarantee Shortfall Shortfall in the total power transfer capability (1000 MW) joint operation of Block-1 and Block-2 & (500MW) for each block individually; INR 0.2 million for each KW or part thereof **. 5.; Shut down duration/ Outage Schedule of Running System (a) Block 1 (b) Block 2 (c) Both Blocks; INR 1 Million per Block for each additional 24 Hours or part thereof^ INR 0.5 Million for each 24 Hours or part thereof^^. ………………………. …………………………………. | Replace the Sub- Clause GCC 23.3(b) in SCC: pay liquidated damages to the Employer in respect of the failure to meet the Functional Guarantees and Shut down duration/ Outage Schedule as specified at Chapter-11 and Clause 1.11 of Part-1 of Technical Specifications, Vol-II of the Bidding Documents and as per rates given here under: S.N; Parameters for levy of liquidated damages on failure to meet the guarantees; Liquidated Damages. 1.; Station Losses for Block-1 & Block-2 individually - a) No load losses(KW) - b) Equivalent load losses (KW); - No load losses@ INR 0.8 million per KW - Equivalent load losses@ 0.4 million per KW. 2.; System Availability Minimum Energy availability requirement for each Block per half year; INR 30 Million for each 0.1% or part thereof for the shortfall below 99.8% down to 98%. 3.; System Reliability a) Equivalent Outage Frequency (EOF) for each Block per half year; a) INR 1 Million for each EOF or part thereof above the guaranteed value. 4.; Station Power Rating Guarantee Shortfall Shortfall in the total power transfer capability (1000 MW) joint operation of Block-1 and Block-2 & (500MW) for each block individually; INR 0.2 million for each KW or part thereof **. 5.; Shut down duration/ Outage Schedule of Running System (a) Block 1 (b) Block 2 (c) Both Blocks; INR 1 Million per Block for each additional 24 Hours or part thereof^ INR 0.5 Million for each 24 Hours or part thereof^^. ………………………. …………………………………. |
|  | Appendix-8(b) (Functional Guarantees), Sample Forms and Procedures, Section-VI | Appendix-8(b) FUNCTIONAL GUARANTEES 1.0 The Facilities and all parts thereof offered shall meet the Functional Guarantees requirements stipulated in Technical Specification. 2.0 The following Guaranteed parameters and respective Guaranteed values of the Facilities and all parts thereof are guaranteed by the Bidder/ Contractor: Sl. No.; Parameter; Guaranteed Values. 1; Rated Station capacity 1. Block-1 2. Block-2 3. Joint operation of Block –1 & Block-2; 1. 500 MW 2. 500MW 3. 1000MW. 2; Station Availability Minimum Energy availability requirement for 1. Block-1 2. Block-2; - ≥ 99.8% - ≥ 99.8%. 3; Station Reliability - (i) Equivalent Outage Frequency for Block-1 per half year a) (ii) Equivalent Outage Frequency for Block-2 per half year - Transient Disturbances per Block per half year; a) (i) ≤ 1 a) (ii) ≤ 1. 4 a); Efficiency No load losses with Converter Transformer set at principal tap* for: 1. Block-1 2. Block-2; (In kW); 1. For Block-1: ………….. 2. For Block-2: …………... b); Equivalent Load Losses (In kW). 1. For Block-1. 2. For Block-2. 5; Thyristor level failure rate ( defined per six months); ≤0.1% per 12 pulse valve group. 8; Guaranteed Failure rate of Relay Module/C&P Module/Component ( defined per six months); ≤ 0.5% except first unit failure. 9; Shutdown of running system (a) Block 1 (b) Block 2 (c) Both Block outage; (a) ≤ 100 days (b) ≤ 100 days (c) ≤ 15 days. In the event of any shortfall in performance of the guaranteed performance of the system / equipments, as mentioned above, the relevant provisions of SCC / GCC in conjunction with the Technical Specification, shall govern. Note: * Principal tap is the Tap Position of converter transformer when HVDC converter shall be delivering 1 PU power (250MW per pole) at nominal DC voltage at keeping ac system voltage 400 KV, 50 Hz at 40 degree Celsius ambient temperature. | Appendix-8(b) FUNCTIONAL GUARANTEES 1.0 The Facilities and all parts thereof offered shall meet the Functional Guarantees requirements stipulated in Technical Specification. 2.0 The following Guaranteed parameters and respective Guaranteed values of the Facilities and all parts thereof are guaranteed by the Bidder/ Contractor: Sl. No.; Parameter; Guaranteed Values. 1; Rated Station capacity 1. Block-1 2. Block-2 3. Joint operation of Block –1 & Block-2; 1. 500 MW 2. 500MW 3. 1000MW. 2; Station Availability Minimum Energy availability requirement for 1. Block-1 2. Block-2; - ≥ 99.8% - ≥ 99.8%. 3; Station Reliability a) (i) Equivalent Outage Frequency for Block-1 per half year a) (ii) Equivalent Outage Frequency for Block-2 per half year; a) (i) ≤ 1 a) (ii) ≤ 1. 4 a); Efficiency No load losses with Converter Transformer set at principal tap* for: 1. Block-1 2. Block-2; (In kW); 1. For Block-1: ………….. 2. For Block-2: …………... b); Equivalent Load Losses (In kW). 1. For Block-1. 2. For Block-2. 5; Thyristor level failure rate ( defined per six months); ≤0.1% per 12 pulse valve group. 8; Guaranteed Failure rate of Relay Module/C&P Module/Component ( defined per six months); ≤ 0.5% except first unit failure. 9; Shutdown of running system (a) Block 1 (b) Block 2 (c) Both Block outage; (a) ≤ 100 days (b) ≤ 100 days (c) ≤ 15 days. In the event of any shortfall in performance of the guaranteed performance of the system / equipments, as mentioned above, the relevant provisions of SCC / GCC in conjunction with the Technical Specification, shall govern. Note: * Principal tap is the Tap Position of converter transformer when HVDC converter shall be delivering 1 PU power (250MW per pole) at nominal DC voltage at keeping ac system voltage 400 KV, 50 Hz at 40 degree Celsius ambient temperature. |
|  | Appendix-10 (Guarantee Declaration), of 1st Envelope, Vol-III of the Bidding Documents | Appendix-10 (Guarantee Declaration) A. For System Performance Guarantee: ………………………. Sl. No; Parameter; Guaranteed Values. 1; Station Power Rating 1. Block-1 2. Block-2 3. Joint operation of Block –1 & Block-2; 1. 500 MW 2. 500MW 3. 1000MW. 2; Station Availability Minimum Energy availability requirement for 1. Block-1 2. Block-2; 1. ≥ 99.8% 2. ≥ 99.8%. 3; Station Reliability a) (i) Equivalent Outage Frequency for Block-1 per half year a) (ii) Equivalent Outage Frequency for Block-2 per half year b) Transient Disturbances per Block per half year; a) (i) ≤ 1 a) (ii) ≤ 1. ………………………………. ………………………………………… | Appendix-10 (Guarantee Declaration) A. For System Performance Guarantee: ………………………. Sl. No; Parameter; Guaranteed Values. 1; Station Power Rating 1. Block-1 2. Block-2 3. Joint operation of Block –1 & Block-2; 1. 500 MW 2. 500MW 3. 1000MW. 2; Station Availability Minimum Energy availability requirement for 1. Block-1 2. Block-2; 1. ≥ 99.8% 2. ≥ 99.8%. 3; Station Reliability a) (i) Equivalent Outage Frequency for Block-1 per half year a) (ii) Equivalent Outage Frequency for Block-2 per half year; a) (i) ≤ 1 a) (ii) ≤ 1. ………………………………. ………………………………………… |
|  | First Envelope and Bid Forms | In view of the above, ‘First Envelope and Bid Forms’ excel stand revised as ‘First_Envelope_and_Bid_Forms_rev01’. Note- Bidders are requested to consider the revised excel ‘First_Envelope_and_Bid_Forms_rev01’ for bid preparation/submission. It may be noted that while submitting the bid, Bidders are required to change the excel file name from ‘First_Envelope_and_Bid_Forms_rev01’ to ‘First_Envelope_and_Bid_Forms’. As per the provisions of the portal, it is mandatory to upload the excel file titled ‘First_Envelope_and_Bid_Forms’ (Bidders may refer user manuals at the portal https://etender.powergrid.in regarding submission of bid). |  |  |
| GCC 33. Change in the Facilities |  |  |  |  |
|  | GCC 33.1.1 | Subject to GCC Sub-Clauses 33.2.5 and 33.2.7, the Employer shall have the right to propose, and subsequently require, that the Project Manager order the Contractor from time to time during the performance of the Contract to make any change, modification, addition or deletion to, in or from the Facilities (hereinafter called “Change”), provided that such Change falls within the general scope of the Facilities and does not constitute unrelated work and that it is technically practicable, taking into account both the state of advancement of the Facilities and the technical compatibility of the Change envisaged with the nature of the Facilities as specified in the Contract. |  | Subject to GCC Sub-Clauses 33.2.5 and 33.2.7, the Employer shall have the right to propose, and subsequently require, that the Project Manager order the Contractor from time to time during the performance of the Contract to make any change, modification, addition or deletion to, in or from the Facilities (hereinafter called “Change”), provided that such Change falls within the general scope of the Facilities and does not constitute unrelated work and that it is technically practicable, taking into account both the state of advancement of the Facilities and the technical compatibility of the Change envisaged with the nature of the Facilities as specified in the Contract. For the purpose of this Clause, Change is broadly categorized in the following three categories: - - Existing item: Any item existing in the BoQ in Contract. - Substituted item: Any item which is to be included in lieu of an existing item in the BoQ in Contract. New item: Any item which was not originally included in the BoQ in Contract. |
|  | GCC 33.2.3 | If before or during the preparation of the Change Proposal it becomes apparent that the aggregate effect of compliance therewith and with all other Change Orders that have already become binding upon the Contractor under this GCC Clause 33 would be to increase or decrease the Contract Price as originally set forth in Article 2 (Contract Price and Terms of Payment) of the Contract Agreement or subsequently amended Contract Price pursuant to GCC Clause 36A (Partial Offloading) hereof, by more than the percentage specified in SCC, the Employer and the Contractor shall mutually agree on specific rates for valuation of the Change beyond the specified percentage. For the said purpose, the Contract Price means the Contract Price of the Facilities notwithstanding the Construction of the Contract. |  | If before or during the preparation of the Change Proposal it becomes apparent that the aggregate effect of compliance therewith and with all other Change Orders that have already become binding upon the Contractor under this GCC Clause 33 would be to increase or decrease the Contract Price as originally set forth in Article 2 (Contract Price and Terms of Payment) of the Contract Agreement or subsequently amended Contract Price pursuant to GCC Clause 36A (Partial Offloading) hereof, by more than the percentage specified in SCC, the Employer and the Contractor shall agree on specific rates for valuation of the Change beyond the specified percentage in the manner specified at GCC Clause 33.2.4.1 b) below. For the said purpose, the Contract Price means the Contract Price of the Facilities notwithstanding the Construction of the Contract. |
|  | GCC 33.2.4 | If rates and prices of any change are not available in the Contract, the parties thereto shall agree on specific rates for the valuation of the change and all matters therein related to the change. Based on the same, the Employer shall, if it intends to proceed with the Change, issue the Contractor with a Change Order. |  | If rates and prices of any change are not available in the Contract, the parties thereto shall agree on specific rates for the valuation of the change and all matters therein related to the change. For arriving at such rates for the valuation of change, following guidelines are hereby specified: - |
|  | GCC 33.2.4.1 | ………………………………………… ………………………………………… |  | For New items: - - If possible, the rate shall be arrived at on the basis of similar item available in the contract. - In case similar item is not available in the Contract, the rate shall be arrived taking into consideration the following documents in the given order of preference: - - POWERGRID SOR (with suitable adjustment in regard to the Price Level) - Analysis of Delhi Schedule of Rates issued by CPWD and considering the declared factor for adjustment. - Based on the rates of that item available in other Contracts/LOAs: For this purpose, average of rates of that item available in other awards placed during last 02 years for the same region, after suitable extrapolation, wherever required, to bring it to current level and after effecting price adjustment, if any, required on account of mismatch of specifications may be used. - Rate(s) established from the lowest budgetary quotation from various manufacturers/suppliers (minimum three nos.) plus 15% to cover Contractor’s profit and overhead. The finalization of new rates in certain cases may be based on the combination of more than one of the guidelines described at Para a) & b) above. |
|  | GCC 33.2.4.2 | ………………………………………… ………………………………………… |  | For Substitute items: For arriving at the rate for Substitute item, the rate for the Existing item (to be substituted) and Substitute item shall be arrived in the similar manner as stipulated at para GCC 33.2.4.1 b) above. (a) If the arrived rate for the Substitute item so determined is more than the arrived rate of the Existing item (to be substituted), the rate payable to the Contractor for the Substitute item shall be the rate for the Existing item (to be substituted) as per Contract so increased to the extent of difference between the arrived rates of Substitute item and the Existing item (to be substituted). (b) If the arrived rate for the Substitute item so determined is less than the arrived rate of the Existing item (to be substituted), the rate payable to the Contractor for the Substitute item shall be the rate for the Existing item (to be substituted) as per Contract so decreased to the extent of difference between the arrived rates of Substitute item and the Existing item (to be substituted). |
|  | GCC 33.2.4.3 | ………………………………………… ………………………………………… |  | Based on the agreed rates for valuation of the change as above and all matters therein related to the change, the Employer shall, if it intends to proceed with the Change, issue the Contractor with a Change Order. |
|  | GCC 33.2.4.4 | ………………………………………… ………………………………………… |  | In case the rate for a New item is finalized on the basis of similar item available in the Contract as per GCC 33.2.4.1 a) above, such rate shall be subject to further Price adjustment as per Appendix-2 to the Contract Agreement, as applicable, to the Contract item based on which the rate has been arrived at. However, for all other cases, the rate so finalized shall not be subject to any further adjustment as per Appendix-2 to the Contract Agreement. |