## Clarification No-I
Clarification No-I dated 01.11.2024 to the bidding documents of Refurbishment of HVDC Control, Protection, SCADA, Valve Hall Equipment and Valve Cooling System for 2x500 MW Chandrapur HVDC Back to Back (BTB) Station under Add-Cap; Specification Number: CC/NT/W-HVDC/DOM/A00/24/12849
Sl. No. | Reference document | Annexure (if applicable) | Clause No. | CLAUSE/DOCUMENT REFERENCE | EXISTING CLAUSE | QUERY DESCRIPTION | POWERGRID REPLY
1 | Section-I: Invitation for Bid (Volume I) |  | 3.3 |  | Bidding will be conducted through the Domestic Competitive Bidding procedures as per the provisions of ITB/BDS and the contract shall be executed as per the provisions of the Contract. | Bidder refers to its email dated 1 Aug 2024. Bidder requests Employer to take necessary steps to enable its participation in bidding for HVDC projects. | Requirement of Bidding documents shall be fulfilled
2 | Section-II: Instruction to Bidders (Volume I) | Annexure-A (BDS) | 3.1.(ii) |  | The Bidder should have supplied, erected, tested and commissioned the equipments for replacement of HVDC Control & Protection System, SCADA System, Valve Cooling Control System and Thyristor Valves for at least one long distance HVDC converter station or a back to back HVDC system of a unit rating of at least 250 MW which has been in Satisfactory Operation* for at least two (2) year after such replacement/renovation work as on the originally scheduled last date of bid submission (soft copy) mentioned above, | It is understood that the Associate of the Qualified Bidder/Contractor in a previous project is permitted to seek qualification as Bidder in this project. For example, let us assume that Company-A was the qualified Bidder/Contractor for Ref-Project. Customer awarded the contracts for this Ref-Project as follows: Offshore Contract to Company-A and Onshore Supply & Services Contracts to Company-B. Company-B is the Associate of Company-A. Company-B's scope in the onshore contracts for this Ref-Project fulfils the requirements of Cl.3.1.(ii). Hence, Company-B fulfils the qualifying requirement as per Cl. 3.1.(ii). Employer is requested to confirm Bidder's understanding. | Provisions of Bidding documents are clear
3 | Section-II: Instruction to Bidders (Volume I) | Annexure-A (BDS) | 3.1.(iii) |  | The Bidder Should have engineered, manufactured, tested, supplied, erected and commissioned HVDC Control & Protection System, SCADA System and Thyristor Valves, for at least one long distance HVDC converter station or a back to back HVDC system of a unit rating of at least 250 MW which has been in Satisfactory Operation* for at least two (2) years as on the originally scheduled last date of bid submission (soft copy) mentioned above. | It is understood that the Associate of the Qualified Bidder/Contractor in a previous project is permitted to seek qualification as Bidder in this project. For example, let us assume that Company-A was the qualified Bidder/Contractor for Ref-Project. Customer awarded the contracts for this Ref-Project as follows: Offshore Contract to Company-A and Onshore Supply & Services Contracts to Company-B. Company-B is the Associate of Company-A. Company-B's scope in the onshore contracts for this Ref-Project fulfils the requirements of Cl.3.1.(ii). Hence, Company-B fulfils the qualifying requirement as per Cl. 3.1.(ii). Employer is requested to confirm Bidder's understanding. | Provisions of Bidding documents are clear
5 | Chapter-1 |  |  |  |  | 1) There are two PDF files for Chapter-1 in the ZIP file: - Chapter 1.pdf (File size: 1078 KB) - Chapter 1 Updated.pdf (File size: 339 KB) Employer is requested to check and confirm which file is valid. 2) There is no Index Sheet provided for Volume-II, which makes it difficult to verify the TS for completeness. Employer is requested to include an Index Sheet mentioning all Chapters and Annexures attached with each Chapter for ease of traceability and readability of the TS. | 1. “Chapter-1 Updated” stands deleted. Bidder shall refer Chapter-1. Please see Amendment-1. 2. The specification is in line with arrangements/ formatting already being followed in previous HVDC tenders of POWERGRID.
6 | Chapter-1 |  | 1.2.(a).(xiii) |  | Space for storage Area is marked in Annexure store Area, approx. 1800 Sqmeter. | 1) As per "Annexure Store Area", an area of 90 m x 23 m has been marked in red. Bidder understands that the closed Store Building of 1800 sqm has to be built over this 90 x 23 sqm area. 2) As per "Annexure Store Area", there are neem trees and a borewell existing in the red-marked area of 90 m x 23 m. Employer is requested to confirm that these existing encumbrances will be removed before starting construction of the new store building. 3) As per "Annexure Store Area", there is an area marked as "New Proposed Sandbed Platform". Employer is requested to confirm whether this platform is part of the HVDC Contractor's scope and if so, provide the size of the platform to be constructed along with the technical specifications. 4) As per "Annexure Store Area", a Semi-closed Store is shown. Employer is requested to confirm whether this semi-closed store is part of the HVDC Contractor's scope and if so, provide the size of the semi-closed store to be constructed along with the technical specifications. | 1)Bidder's understanding is in line with TS requirement. 2)The site preparatory work is in the scope of the bidder.Please refer Amendment -1. 3) The bidder's scope is limited to covered storage Area only as per TS. 4) The bidder's scope is limited to covered storage Area only as per TS.
7 | Chapter-1 |  | 1.3.1 |  | The Contractor shall be responsible for overall system engineering studies and detailed design for all elements, systems, facilities and equipment. | Bidder understands that the HVDC Contractor has to carry out all studies for both directions of power flow. | Bidder's understanding is in line with TS requirement
8 | Chapter-1 |  | 1.3.1 |  | The Contractor shall be responsible for overall system engineering studies and detailed design for all elements, systems, facilities and equipment. | Bidder understands that the HVDC Contractor has to carry out the studies for minimum 4 network scenarios i.e. peak load, light load, extremely weak and islanded mode. | Bidder's understanding is in line with TS requirement
9 | Chapter-1 |  | 1.3.1 |  | The Contractor shall be responsible for overall system engineering studies and detailed design for all elements, systems, facilities and equipment. | Employer is requested to check and confirm if Power Oscillation Damping studies are to be carried out in this project. | Power Oscillation Damping studies shall be carried out by the bidder.
10 | Chapter-1 |  | 1.3.1.(b) |  | ...studies for integration of the HVDC system in to the existing HVDC/HVAC system... | 1) Bidder understands that the HVDC Contractor shall be responsible for carrying out Interaction Studies between Chandrapur BtB HVDC station and all nearby existing / upcoming HVDC stations such as MSETCL's 1500 MW HVDC station at Chandrapur (part of Chandrapur-Padghe scheme), 6000 MW Nagpur HVDC station (part of KPS2-Nagpur scheme), FACTS devices (under implementation / in planning), Inverter based Resources (IBR) and Inverter based Loads which are electrically coupled nearby. 2) Employer is requested to provide the list of all HVDC stations, FACTS devices, IBRs, etc. which are electrically coupled nearby to the Chandrapur Back to Back station - existing, under implementation and in planning. | 1) Bidder's understanding is in line with TS requirement 2) The network file will be provided to the successful bidder.
11 | Chapter-1 |  | 1.3.1.(b) |  | ...studies for integration of the HVDC system in to the existing HVDC/HVAC system... | Bidder understands that Commutation Failure Performance Study to evaluate the impact of commutation failure & cascading commutation failure (if expected) on the associated AC network shall be carried out by the HVDC Contractor. | Bidder's understanding is in line with TS requirement
12 | Chapter-1 |  | 1.3.1.(e) |  | Studies to ensure and demonstrate that the nearby generators including those at Chandrapur & Warora in Western grid and Ramagundam in Southern grid shall not be adversely affected by the HVDC system, particularly with regard to SSO/SSR and harmonic injection. | 1) Bidder understands that Sub Synchronous Control Interaction Study corresponding to RE plants (IBR based) shall be carried out by the HVDC Contractor. 2) Bidder notes that "Annexure Generator" contains list of all nearby synchronous generators. Employer is requested to provide list of all IBR based RE plants which are electrically coupled nearby to the Chandrapur Back to Back station - existing, under implementation and in planning. | 1)Bidder's understanding is in line with TS requirement as applicable. 2) The network file will be provided to the successful bidder.
13 | Chapter-1 |  | 1.3.3.4 |  | As per CEA (Central Electricity authority) the Guidelines for validity period of type test(s) conducted on Major Electrical equipments in Power Transmission system is available in the CEA website at the link http://cea.nic.in/reports/ others / ps / psetd / Approved_Type%20test%20validity%20guidelines. | 1) Employer is requested to check and verify the website link. Bidder understands that the following link is to be referred: https://cea.nic.in/wp-content/uploads/notification/2021/09/Amended_CEA_Guideline_of_Type_Test_Validity_17092021.pdf 2) Bidder understands that provisions of TS Cl. 1.3.3.4.(a) to (c) below will prevail over CEA Guidelines referred in this clause. For example, Thyristor Valves shall be necessarily type tested under this contract and type test report shall be approved by the Employer [as per TS Cl.1.3.3.4.(a)] even if the CEA Guidelines do not mandate repetition of type test as on date or at later date. 3) Bidder understands that the CEA Guidelines prevailing 15 days before the originally scheduled last date of bid submission (soft copy) shall be considered in accordance with TS Cl. 3.2. | 1) Please refer Amendment-1 2)Bidder's understanding is in line with TS requirement. 3)Bidder's understanding is in line with TS requirement.
14 | Chapter-1 |  | 1.3.4 |  | (ii) ...Additional Civil work for installation of new equipment like cooler fans foundation, valve cooling system, new store building etc…. (iii) Valve Cooling UPS battery building as per Annexure Battery Room | TS is silent / not clear regarding the following requirements for Store Building & Valve Cooling UPS Battery Buildings: 1. Illumination system 2. Electrical Distribution system 3. Rainwater Harvesting system Owner is requested to confirm if above facilities are required or not, and accordingly specify the minimum requirements. | The following are requirements for Store Building & Valve Cooling UPS Battery Buildings: 1. Illumination system - under present scope of Bidder 2. Electrical Distribution system - under present scope of Bidder 3. Rainwater Harvesting system - not in present scope of bidder The details of above facilities shall be decided during detailed engineering.
15 | Chapter-1 |  | 1.3.4.(ii) |  | Additional Civil work for installation of new equipment like cooler fans foundation, valve cooling system, new store building etc. | Bidder refers to "Annexure Store Area" and understands that following additional civil works shall be carried out by the HVDC Contractor: a) Peripheral road along with walkway, drainage & street lighting shall be provided around the new store building and other storage areas if applicable (e.g. semi-closed store, sandbed platform, etc.). The peripheral road shall be connected to the nearest existing access road. b) Peripheral fencing along with main gate shall be provided around the new store building and other storage areas if applicable (e.g. semi-closed store, sandbed platform, etc.) for security purpose. Employer is requested to confirm if above facilities are required or not, and accordingly specify the minimum requirements by marking these in the layout drawing (Annexure Store Area). | a)Only Closed store as per Annexure Store area rev01 is under the scope.Please refer Amendment -1 b) Bidder's understanding is in line with TS requirement.
16 | Chapter-1 | Annexure Battery Room |  |  | The size of the rooms shall be decided by the bidder as per their design. However, the minimum height of the room shall be 3100mm. | 1) Employer is requested to provide preliminary layout drawing (external & internal) of the Battery Building and mention the minimum requirements. 2) Employer is requested to mark the areas to be developed for construction of the 2 Battery Buildings in the existing station layout (similar to Annexure Valve Cooling Area). 3) Employer is requested to confirm the height of 3100 mm mentioned in the clause refers to the Eave Height. | 1)The design of layout of is under the scope of the bidder. 2) The Battery buildings shall be built close to the valve cooling room. Bidder may visit the site to familiarize with the requirements. 3) Confirmed.
17 | Chapter-1 |  | 1.3.4.1 |  | a) Site preparation including dismantling the existing facilities to accommodate new equipments in the scope of work as per TS. b) Any Civil works, if required, related to Valve Hall, Valve Cooling System, Valve Cooling UPS, PLC equipment and Cable Trench to be covered in the present scope of work as per TS. c) New Store Building in the scope of work as per TS. | Bidder understands that following site preparation & civil works are included in present scope of HVDC Contractor: 1. Site filling & leveling up to minimum FGL (to be specified by Owner) for Store Building, Outdoor Cooler Fans, Valve Cooling System UPS Battery Buildings & associated peripheral areas. 2. Modification including extension of roads, fencing & drains for interface to Store Building, Outdoor Cooler Fans, Valve Cooling System UPS Battery Buildings & associated peripheral areas. 3. Modification including extension of cable trenches, earthing, etc. for interface to Store Building, Outdoor Cooler Fans, Valve Cooling System UPS Battery Buildings & associated peripheral areas. Employer is requested to confirm Bidder's understanding. | 1. Bidder's understanding is in line with TS requirement. 2.Bidder's understanding is in line with TS requirement except for access road to store area, which is excluded from scope.. 3.Bidder's understanding is in line with TS requirement.
18 | Chapter-1 |  | 1.3.4.1.(c) |  | New Store Building in the scope of work as per TS. | 1) No layout drawing has been provided for the closed Store Building. Bidder requests Employer to provide the same, showing the minimum requirements. 2) Employer is requested to confirm whether any rooms for Employer's staff e.g. store-in-charge room, meeting room, etc. are required or not. 3) Employer is requested to confirm whether any of the following facilities is required in the Store Building - whether for Employer's staff rooms or for storage areas: a) Air conditioning b) Potable water facilities c) Sanitary facilities d) Electrical distribution & lighting e) Communication facilities viz. wifi router, intercom. f) Office furniture e.g. tables, chairs, cupboards, etc. In case any of the above facilities is required, Employer is requested to specify the minimum requirements and/or provide the techncial specifications. | 1) The design of layout of the store Building is in the scope of the contractor. The requirements are as per Chapter-8 of TS. 2) Employer's staff is required in the new Store building.Please refer Amendment -1 . 3) The following are the requirement inn the new store building: a) Air conditioning - under present scope of bidder b) Potable water facilities - under present scope of bidder c) Sanitary facilities - under present scope of bidder d) Electrical distribution & lighting - under present scope of bidder e) Communication facilities viz. wifi router, intercom. - not in scope. f) Office furniture e.g. tables, chairs, cupboards, etc. - not not in scope.
19 | Chapter-1 |  | 1.3.4.1.(c) |  | New Store Building in the scope of work as per TS. | TS is silent / not clear regarding the following requirements for Store Building & Valve Cooling UPS Battery Buildings: 1. Permanent furnishings e.g. storage racks, storage bins, signage boards, etc. 2. Permanent material handling arrangements e.g. mobile gantry cranes, chain pulley with electrically operated hoists, hand operated pallet / platform trolleys, loading / unloading facilities, etc. Employer is requested to confirm if above facilities are required or not, and accordingly specify the minimum requirements. | 1. Not in scope 2. Not in scope.
20 | Chapter-1 |  | 1.3.5.4 |  | All equipment during storage shall be protected against damage due to act of nature or accidents. | 1) In order to meet this requirement in the closed Store Building , Bidder understands that suitable fire detection & fighting system e.g. portable fire extinguishers, etc.would be required. Employer is requested to check & confirm the minimum requirements. 2) For other storage areas e.g. semi-closed store building, sandbed platform, etc. (if required), Employer is requested to check & confirm the minimum requirements. | 1) Fire detection and portable fire extinguishers is included in bidder's scope. 2))Only Closed store as per Annexure Store area rev01 s under the scope. Please refer Amendment -1.
21 | Chapter-1 |  | 1.3.5.4 |  | Sensitive equipments shall be stored indoors under controlled environment, if required. | 1) No layout drawing has been provided for the closed Store Building. Employer is requested to provide the layout drawing and earmark areas therein for storage of equipment / spares requiring controlled environment i.e. temperature / humidity / dust ingress controls. 2) Bidder requests Employer to specify a minimum area (e.g. 8m x 6m) wherein appropriate air condition system is installed and dust ingress protection measures deployed. | 1) The design of layout of the store Building is in the scope of the contractor. The requirements are as per Chapter-8 of TS. 2) Please refer Amendment -1.
22 | Chapter-1 |  | 1.4.3 |  | For the first 30 days after start of trial operation of both poles / blocks, there shall be one engineer of the Contractor on a round the clock basis. | Bidder understands that the 30 days will end after date of first time start of trial operation of both blocks. In other words, there will be no extension in case the trial operation has to be restarted for any reasons. | No extension is required in case the trial operation has to be restarted for any reasons.
23 | Chapter-1 |  | 1.4.3 |  | After 30 days and up to the end of the guarantee period there shall be at least one engineer of the Contractor at Converter station site who shall follow the regular office hours and shall be available at site within one hour if required, during other times. | Bidder understands that the "end of guarantee period" referred in this clause is the end of Reliability and Availability Monitoring (RAM) period in accordance with Chapter 11 of TS. | Guarantee period referes to defect liability period.
24 | Chapter-1 |  | 1.4.5 |  | In addition, the following Performance Guarantees in respect of equipment being replaced/installed under present scope shall be provided by the Contractor, as detailed in the specification, and liquidated damages shall be payable by the Contractor in the event of shortfall in any of the guaranteed values of : i. Energy Availability ii. Reliability iii. Station power rating iv. Thyristor failure rate v. Relay module/C & P module/Component failure rate vi. Shutdown Duration | Bidder understands that HVDC Contractor shall also be responsible for meeting performance guarantee in respect of Station Efficiency in accordance with TS Cl. 11.10. Employer is requested to include this in the bullet list to avoid conflict of understanding. | Please refer Amendment-1.
25 | Chapter-1 |  | 1.7.(iii) |  | Trial-Operation: Operation of the Facilities or any part thereof by the Contractor immediately after the Commissioning for a continuous period as specified in the Technical Specifications under Sub-Clause 9.3.7 Trial Operation. | In accordance with Annexure - Outage Schedule, Bidder understands that Taking Over of the Facilities by the Employer shall occur only after completion of 10-days trial operation of both blocks simultaneously post-refurbishment. | Bidder's understanding is in line with TS requirement.
26 | Chapter-1 |  | 1.8 |  | In case the bidder proposes to get the civil/erection works executed through sub-contractors, then such sub-contractors must have at least two years experience in executing such works of similar value. | Bidder understands that the 2 years experience will be counted from the originally scheduled last date of bid submission (soft copy) i.e. 7 Oct 2024. | Bidder's understanding is in line with TS requirement.
27 | Chapter-1 |  | 1.8 |  | Contractor shall bear all electricity charges under the present scope of work till the commissioning of the project (DOCO) which includes testing and commissioning of all the equipments. | 1) Bidder understands that DOCO refers to Date of Commercial Operation or Deemed Date of Commercial Operation (whichever is earlier) declared by the Employer to authorities like CERC, GRID-INDIA, etc. 2) In case the Taking Over of the Facilities by the Employer occurs after DOCO, Bidder understands that the electricity charges from DOCO up to the date of Taking Over will be borne by the Employer. | 1)Bidder's understanding is in line with TS requirement. 2)Bidder's understanding is in line with TS requirement.
28 | Chapter-1 |  | 1.8.1.1 |  | The following HVDC equipment shall be offered from a regular manufacturer(s) who have been manufacturing such equipment(s) for HVDC system for the last (5) five years or more as on the originally scheduled date of the bid opening and should have been in operation for at least two (2) years as on the originally scheduled date for the dead line for submission of bid. | A provision of this clause contradicts Cl. 3.1.(i) of Annexure-A (BDS) which states: "The Bidder shall be a regular manufacturer of High voltage Direct Current Transmission equipment who have been manufacturing such equipment for the last five (5) years or more as on the originally scheduled last date of bid submission (soft copy) i.e. 07.10.2024." Employer is requested to check and confirm. | Please refer Amendment-1.
29 | Chapter-1 |  | 1.8.1.1.(a).(i) |  | The Indian manufacturer should have an association/collaboration with the principal manufacturer who meets the requirements of clause 3.1 of QR specified in Section-EQC, Part- I of the Bidding Documents. | "Section-EQC" could not be found in the bidding documents. Bidder understands that this is a typographic error, and the document to be actually referred is Annexure-A (BDS). Employer is requested to confirm Bidder's understanding. | Please refer Amendment-1
30 | Chapter-1 |  | 1.8.1.1.(a).(ii) |  | In case, the Manufacturer offers their latest version of HVDC Control and Protection System and which is not in operation as on the date of NOA, the same shall also be acceptable however, the defect liability period of the same shall be 05 years from DOCO. | Bidder understands that DOCO refers to Date of Commercial Operation or Deemed Date of Commercial Operation (whichever is earlier) declared by the Employer to authorities like CERC, GRID-INDIA, etc. | Bidder's understanding is in line with TS requirement.
31 | Chapter-1 |  | 1.8.1.1.(a).(ii) |  | The Indian manufacturer should have an association / collaboration with the parent company who meets the requirements of clause 3.1 of QR specified in Section-EQC, Part- I of the Bidding Documents. | 1) "Section-EQC" could not be found in the bidding documents. Bidder understands that this is a typographic error, and the document to be actually referred is Annexure-A (BDS). 2) Bidder understands that association / collaboration with Group Company is also permitted in accordance with Annexure-A (BDS). Employer is requested to confirm Bidder's understanding. | 1)Please refer Amendment-1 . 2)Please refer Amendment-1 .
32 | Chapter-1 | Annexure Outage Schedule | 1.11 |  | Contractor shall ensure that, during preparatory work in station for replacement, before availing outage, no effect on running HVDC system. | 1) Bidder understands that the Preparation Time for Block-1 Outage (7 days specified), Preparation Time for Block-2 Outage (7 days specified) and Preparation Time for Both Blocks Outage (7 days specified) are indicative only. In other words, Preparation TIme for Block-1 / Block-2 / Both Blocks may be exceeded without impacting the running of the respective Block(s). 2) As per TS, HVDC Contractor has to carry out pre-refurbishment measurements of different parameters like harmonics, radio interference, audible noise, etc. before the outage of first Block. In order to avoid conflicts during execution, Employer is requested to incorporate these activities in the table: - Pre-refurbishment measurements for Block-1 (Block-2 not in operation) - Pre-refurbishment measurements for Block-2 (Block-1 not in operation) - Pre-refurbishment measurements for Block-1 & Block-2 The actual dates / durations can be mutually discussed & agreed during execution. | 1)Bidder's understanding is in line with TS requirement. 2) Please refeer Amendment-1
33 | Chapter-1 |  | 1.15 |  | GRID CONTROLLER OF INDIA LIMITED (formerly known as Power system operation Corporation limited) is system operation arm of Government of India has published the procedure for first time charging/Energisation (FTC). Latest guidelines which are available in GRID – INDIA website for first time charging is to be mandatorily complied by the Contractor. | 1) The procedure published by GRID-INDIA is applicable to the Transmission Asset Owner (in this case the Employer) and contains several obligations that may be acceptable to Employer in its role as Transmission Asset Owner. On the other hand, the Contractor has limited role / scope as per the contract that will be signed with the Employer. Contractor cannot be expected to take over all responsibilities of the Employer. 2) Please refer Bidder's email dated 21 Sep. 2023 & other submissions addressed to PGCIL wherein comments have been provided on GRID-INDIA's procedure. Owner will be responsible for suitably screening the technical data / models / reports submitted by the HVDC Contracto, and submit only necessary extracts of technical info to GRID-INDIA based on "need-to-know" principle. Furthermore, Owner shall safeguard confidentiality of all technical info submitted by the HVDC OEM, and therefore ensure that a mutually acceptable, project specific non-disclosure agreement (NDA) is signed by all 3rd party recipients e.g. GRID-INDIA beforehand. | 1) The Bidder's complinace requirement is limited to the scope of the contract as per TS. 2)The proceudre for first time charging being a statutory requirement, shall be complied. No separate NDA shall be applicable.
34 | Chapter-1 |  | 1.15 |  | GRID CONTROLLER OF INDIA LIMITED (formerly known as Power system operation Corporation limited) is system operation arm of Government of India has published the procedure for first time charging/Energisation (FTC). Latest guidelines which are available in GRID – INDIA website for first time charging is to be mandatorily complied by the Contractor. | 1. Bidder requests Owner to confirm relevance / applicability of "NLDC Operating Procedure 2024" available on GRID-INDIA's website: https://posoco.in/en/download/nldc-operating-procedure-2024/?wpdmdl=58854 Owner is requested to identify the relevant chapters / sections that are relevant for the HVDC Contractor e.g. Chapter 8, 16, 17, etc. 2. Bidder understands that the cut-off date for applicability of GRID-INDIA's Guidelines / Procedures referred in this clause would be as per TS Clause 3.2 i.e. 15 days before the originally scheduled last date of bid submission (soft copy). | 1)The relevant clauses as applicable may be complied. 2) Bidder's understanding is in line with TS requirement.
35 | Chapter-2 |  | 2.2.1 |  | Data of each Pole - Rating: 500MW | Bidder understands that the rated capacity is applicable for both directions of power flow. | Bidder's understanding is in line with TS requirement.
36 | Chapter-2 |  | 2.2.1 |  | Overload Details of both Poles: The Chandrapur HVDC scheme is designed for continuous operation at 2x500MW (1 pu power transmission is defined as 1000MW) at maximum ambient temperature. The scheme is also designed with a two hour overload rating of 2x550MW at maximum ambient temperature (1.1pu power transmission, 1100MW; when all redundant coolers and heat exchangers are in service.....The overload capability as above shall be provided on both individual as well as combined operation of pole 1 & 2. | Bidder understands that the rated & overload capacities are applicable for both directions of power flow. | Bidder's understanding is in line with TS requirement.
37 | Chapter-2 |  | 2.2.1 |  | Overload Details of both Poles: The Chandrapur HVDC scheme is designed for continuous operation at 2x500MW (1 pu power transmission is defined as 1000MW) at maximum ambient temperature. The scheme is also designed with a two hour overload rating of 2x550MW at maximum ambient temperature (1.1pu power transmission, 1100MW; when all redundant coolers and heat exchangers are in service.....The overload capability as above shall be provided on both individual as well as combined operation of pole 1 & 2. | Bidder understands that HVDC Contractor shall be responsible for carrying out field tests post-refurbishment to verify the rated & overload capacities specified in this clause for both directions of power flow. | Bidder's understanding is in line with TS requirement.
38 | Chapter-4 |  | 4.11.7 |  | The Contractor shall limit the audible noise for various areas of the converter station and buildings in his scope of work to the following values and demonstrate by calculation and site measurement that the specified levels shall not be exceeded. Mechanical Equipment Indoor areas having long term access (measured at 2 meter distance) : 75 dBA Equipment in outdoor areas (measured at 15 meter distance) : 75 dBA | 1) As per scope of work specified in Chapter-1, the HVDC Contractor's main areas of work will be as follows: a) Valve Hall b) Control Room / Control Equipment Room in Service Building c) Valve Cooling System Room (where pump skid will be placed) d) Outdoor Coolers for Valve Cooling System e) Valve Coolng Sytem UPS Battery Building f) Store Building Except c) and d), the TS is silent regarding applicable audible noise limits for a), b), e) and f). Employer is requested to check and confirm that audible noise limits have to be met only for c) & d) above. 2) The audible noise limit for Mechanical Equipment Indoor Areas specified in Cl. 4.11.7 contradicts the limit specified in Cl. 4.11.6 of "Annexure Interference & Audible Noise Levels". Employer is requested to check and resolve the discrepancy. | 1)Bidder's understanding is correct, compliance for audible noise is limited as per TS. 2) Please refer Amendment-1
39 | Chapter-8 |  | 8.9.7 |  | Size : About 18mx80M (without any internal columns) Eave height : 7.0m clear under the knee | 1) As per "Annexure Store Area", an area of 90 m x 23 m has been marked in red. As per TS Cl. 1.2.(a).(xiii), space for closed Store Building of 1800 sqm has been specified. In TS Cl. 8.9.7, the Store Building size of 18 m x 80 m has been specified. Employer is requested to check and confirm the size of the new Store Building. 2) Employer is requested to provide external and internal layout drawing of the Store Building. | 1) Please refer Amendment-1 2) The design of layout of the store Building is in the scope of the contractor. The requirements are as per Chapter-8 of TS.
40 | Chapter-8 |  | 8.9.7 |  | Wall mount fans-20 nos. and Industrial exhaust fans 8 nos. | As per TS Cl. 1.3.5.4, "Sensitive equipments shall be stored indoors under controlled environment, if required." Bidder requests Employer to specify a minimum area (e.g. 8m x 6m) wherein appropriate air condition system is installed and dust ingress protection measures deployed. | Please refer Amendment-1 .
41 | Chapter-8 |  | 8.9.7 |  | All Civil, Electrical and services works. | TS is not clear regarding the requirements of "Electrical and services works" pertaining to the Store Building. Employer is requested to specify the minimum requirements for the various faciltiies required e.g. - Illumination system - HVAC system - Fire fighting & detection system - Access control system - CCTV system - Material handling system e.g. cranes, hoists, etc. - Office LAN, Wifi, etc. facilities - Employer's staff facilities e.g. furniture, potable water facilities, sanitary facilities. etc. | Illumination system - included in present scope HVAC system - included in present scope Fire fighting & detection system - included in present scope Access control system - not required CCTV system - not required Material handling system e.g. cranes, hoists, etc. - not required Office LAN, Wifi, etc. facilities - not required Employer's staff facilities e.g. furniture, potable water facilities, sanitary facilities. - furniture not required, potable water facilities and sanitary facilities to be provided
42 | Chapter-8 |  | 8.9.7 |  | All Civil, Electrical and services works. | TS is not clear regarding the requirements of "Civil works" pertaining to the Store Building. Employer is requested to specify the minimum requirements for the various faciltiies required e.g. - Open storage yards (PCC/RCC/Sandbed) - Semiclosed storage sheds - Access road to Store Building and associated areas. - Peripheral roads around Store Building and associated areas. - Fencing around Store Building and associated areas. - Walkways for personnel movement around Store Building and associated areas. - Connection to existing plant drainage system. - Loading & unloading platform with ramp. - Rainwater harvesting system - Civil works for potable water & sanitary facilities. etc. | - Open storage yards (PCC/RCC/Sandbed) - not under the scope - Semiclosed storage sheds - not under the scope. - Access road to Store Building and associated areas.- not under the scope - Peripheral roads around Store Building and associated areas.- not under the scope - Fencing around Store Building and associated areas. - included in present scope - Walkways for personnel movement around Store Building and associated areas.- included in present scope - Connection to existing plant drainage system.- included in present scope - Loading & unloading platform with ramp.- included in present scope - Rainwater harvesting system- not included in present scope - Civil works for potable water & sanitary facilities.- included in present scope
43 | Chapter-8 |  | 8.9.7.6 |  | For day lighting purpose of GIS hall, minimum 2 mm thick approved translucent polycarbonate sheet shall be provided for wall lighting in addition to windows for at least 10% of wall area on upper portion of both long walls. | Bidder understands that the "GIS hall" mentioned in this clause refers to the "Closed Store Building". Employer is requested to correct the typographic error. | Clause 8.9.7 is the specification for Pre - Engineered Store building, and "GIS hall" mentioned at clause 8.9.7.6 may be read as "closed store building".
44 | Chapter-8 |  | 8.9.11 |  | Construction of new foundations for the coolers, further any modification/ refurbishment/ making good of existing road for crossing of cooling pipes is also in the scope of work. | In case existing roads cannot be used for crossing of the cooling pipes, Bidder shall supply & install suitable overhead steel structure. Employer is requested to confirm acceptance. | Bidder's understanding is in line with TS requirement.
45 | Chapter-11 |  | 11.2 |  | The Guaranteed parameters as stated below to be established by the contractor for Block 1 with 500 MW in parallel operation with Block 2 with 500 MW are :- - Station Power rating - Availability - Reliability - Station Efficiency (Station Loss) - Thyristor failure Rate - Guaranteed failure Rate of Relay module/C&P module /components | Bidder understands that HVDC Contractor shall also be responsible for meeting performance guarantee in respect of Outage Duration for refurbishment in accordance with Annexure - Outage Schedule. | Bidder's understanding is in line with TS requirement.
46 | Chapter-11 |  | 11.4.1.1.3 |  | A disturbance, caused by a failure or mal-operation of the control and/or protection system, that causes a substantial change of dc power & resulting in the transmitted power to be less than or equal to the minimum power level for a duration of less than or equal to 100 ms is defined to be a transient disturbance and shall not be considered as a forced outage. Transient disturbance that develop into outage lasting for more than 100 ms shall be counted as forced outage. | There is contradiction in the definition of Transient Disturbance in this clause and TS clause 11.6. As per Cl. 11.4.1.1.3, the duration mentioned for Transient Disturbance is less than 100 ms. As per Cl. 11.6, the duration mentioned for Transient Disturbance is more than 20 ms. Employer is requested to check and clarify the discrepancy. | Please refer Amendment-1 .
47 | Chapter-11 |  | 11.4.1.3 |  | 11.4.1.3 ODF = Po / PmOutage Duration Terms | Bidder understands that the formula "ODF = Po/Pm" is part of the previous clause 11.4.1.2.3. Employer is requested to correct the typographic error. | Please refer Amendment-1 .
48 | Chapter-11 |  | 11.4.1.4.1 |  | In a full year the Period Hours are 8760 h (8784 h for a leap year). If the equipment is commissioned part way through a year the period hours shall be proportionately less than 8760 h. (This shall not be applicable for verification of guarantees). | Bidder understands that the performance monitoring shall be done on per block basis in periods of six months each. Hence, Employer is requested to modify the clause as follows: "In a full half year the Period Hours are 8760 4380 h (8784 4404 h for a leap half year). If the equipment is commissioned part way through a half-year the period hours shall be proportionately less than 8760 4380 h." | Please refer Amendment-1.
49 | Chapter-11 |  | 11.4.1.5.4 |  | Reliability is expressed in terms of the number of forced outages of curtailment occurrences of Block per unit of time, usually one year. | Bidder understands that the performance monitoring shall be done on per block basis in periods of six months each. Hence, Employer is requested to modify the clause as follows: "Reliability is expressed in terms of the number of forced outages of curtailment occurrences of Block per unit of time, in this project this shall be a period of six consecutive months usually one year." | Please refer Amendment-1 .
50 | Chapter-11 |  | 11.5.2 |  | The operation of the 2x500 MW block-1 & 2 shall be monitored during the guarantee period of minimum 12 months by a data base software developed by the Contractor incorporating details as specified under clause 11.4 to determine whether it meets the guarantees. | Bidder understands that the performance monitoring shall be done on per block basis in periods of six months each. Hence, Employer is requested to modify the clause as follows: "The operation of the 2x500 MW block-1 & 2 shall be monitored during the guarantee period on per block basis for duration of minimum two consecutive periods of 6 12 months each by a data base software developed by the Contractor incorporating details as specified under clause 11.4 to determine whether it meets the guarantees." | Please refer Amendment-1 .
51 | Chapter-11 |  | 11.7.1 |  | The period basis for availability and reliability calculations shall be 12 consecutive months (one year). The period over which the guarantees are to be in effect shall be twelve (12) months (i.e. one year), or any valid extension thereof, commencing six months after successful completion of trial operation of each 500 MW block . | 1) Bidder understands that the monitoring of various performance guarantee parameters such as availability, reliability, failure rates, etc. shall be done on per block basis in periods of six months each, for minimum two periods of six months each. 2) Bidder understands that the performance monitoring period for availability, reliability, failure rates, etc. shall commence six months after successful completion of trial operation of both 500 MW blocks simultaneously. 3) There are contradictions within the clause as clarified in 1) & 2) above. Hence, Employer is requested to modify the clause as follows: "The period basis for availability, and reliability, failure rate, etc. calculations shall be 6 12 consecutive months (one half-year). The period over which the guarantees are to be in effect shall be two consecutive periods of six (6) twelve (12) months (i.e. one two half-years), or any valid extension thereof, commencing six months after successful completion of trial operation of each both 500 MW blocks simultaneously." | Please refer Amendment-1 .
52 | Chapter-11 |  | 11.8.1 |  | Also, subject to the terms and conditions specified, the availability per year, considering forced outages, shall be equal to or exceed the guaranteed value. | There are contradictions within the clause. Bidder understands that the performance monitoring shall be done on per block basis in periods of six months each. Hence, Employer is requested to modify the clause as follows: "Also, subject to the terms and conditions specified, the availability per six months year, considering forced outages, shall be equal to or exceed the guaranteed value." | Please refer Amendment-1 .
53 | Chapter-11 |  | 11.8.2.(a) |  | If the annual energy availability, averaged over the 12 months (one year) guarantee period, proves to be below the guaranteed value, the guarantee period shall be extended by six months. If at the end of this six months, the one year average energy availability, disregarding the half year ( any 6 consecutive months) with the lowest availability is equal to or higher than the guaranteed value, then the availability guarantee shall be considered as fulfilled. | There are contradictions within the clause. Bidder understands that the performance monitoring shall be done on per block basis in periods of six months each. Hence, Employer is requested to modify the clause as follows: "If the semi-annual energy availability, averaged over the 6 12 months (one year) guarantee period during the two consecutive periods of 6 months each, proves to be below the guaranteed value, the guarantee period shall be extended by six months. If at the end of this six months, the one year average energy availability over 6 months in any two out of three periods of six months each, disregarding the half year ( any 6 consecutive months) with the lowest availability is equal to or higher than the guaranteed value, then the availability guarantee shall be considered as fulfilled." | Please refer Amendment-1.
54 | Chapter-11 |  | 11.8.2.(b) |  | If the annual energy availability averaged over the best one year period is still below the guaranteed value, the Contractor shall correct all design deficiencies and equipment defects at no cost to the Employer. | There are contradictions within the clause. Bidder understands that the performance monitoring shall be done on per block basis in periods of six months each. Hence, Employer is requested to modify the clause as follows: "If the semi-annual energy availability averaged over the best two one year periods of six months each is still below the guaranteed value, the Contractor shall correct all design deficiencies and equipment defects at no cost to the Employer." | Please refer Amendment-1 .
55 | Chapter-11 |  | 11.8.2.(c) |  | After correction of such deficiencies and defects, if the annual energy availability averaged over a further half year period (excluding the previous one and half year period and the period for correcting such deficiencies) is still below the guaranteed value, liquidated damages calculated as given below shall be paid by the Contractor to the Employer. | There are contradictions within the clause. Bidder understands that the performance monitoring shall be done on per block basis in periods of six months each. Hence, Employer is requested to modify the clause as follows: "After correction of such deficiencies and defects, if the semi-annual energy availability averaged over a further half year period (excluding the previous one and half year period and the period for correcting such deficiencies) is still below the guaranteed value, liquidated damages calculated as given below shall be paid by the Contractor to the Employer." | Please refer Amendment-1 .
56 | Chapter-11 |  | 11.9.2.(a) |  | If the number of occurrences/six monthly (EOF/TD) averaged over the 12 months (one year) guarantee period exceeds the guaranteed value, the guarantee period shall be extended by six months. If, at the end of the extended period the one year average number of occurrences/6 months, disregarding any six consecutive months with the highest number of occurrences/6 months, is equal to or lower than the guaranteed number of occurrences/6 months then the reliability guarantee shall be considered as fulfilled. | There are contradictions within the clause. Bidder understands that the performance monitoring shall be done on per block basis in periods of six months each. Hence, Employer is requested to modify the clause as follows: "If the number of occurrences/six monthly (EOF/TD) averaged over during the two consecutive periods of 6 12 months each (one year) guarantee period exceeds the guaranteed value, the guarantee period shall be extended by six months. If, at the end of the extended period the one year average number of occurrences/6 months in any two out of three periods of six months each, disregarding any six consecutive months with the highest number of occurrences/6 months, is equal to or lower than the guaranteed number of occurrences/6 months then the reliability guarantee shall be considered as fulfilled." | Please refer Amendment-1 .
57 | Chapter-11 |  | 11.10.2.1 |  | The losses shall be determined for Block 1/2 operation under nominal conditions of ac Busbar voltage (400 KV ), dc voltage (at the rectifier), frequency (50.0 Hz), commutating reactance and firing angles, and with reactive compensation equipment connected from the installed banks and sub banks so as to result in as close to unity power factor operation of the converter station as a whole as possible subject to achieving the harmonic performance levels specified. | Bidder wishes to draw Employer's attention to the Bid Opening of previous HVDC projects - wherein other Bidder(s) quoted lower losses due to possible misinterpretation of the provisions of this clause. In order to avoid such conflicts, Employer is requested to specify the requirements clearly and without ambiguity, by adding supplementary text as below: 1) In all cases, the reactive power exchange of the HVDC station shall not exceed the limits specified in TS Cl. 4.3 and 2.4.3. 2) Employer is requested to specify the harmonic performance limits to be met, while simultaneously meeting the reactive power exchange limits. | TS is clear in this regard.
58 | Chapter-11 |  | 11.10.4 |  | The Employer undertakes to make an evaluation of no load and Equivalent Load Losses stated by the Bidder in his bid. | Bidder appreciates Employer's intent to evaluate losses at bid stage as well as during execution. In order to ensure fair bidding process, Employer is requested to additionally specify maximum limits for the no-load losses (per block) and equivalent load losses (per block). The evaluation of losses shall however be done based on actual losses quoted by the respective Bidder (subject to the losses being lower than the maximum limits specified). | TS is clear in this regard.
59 | Chapter-11 |  | 11.11 |  | The necessary field tests shall be performed after the trial operation period to demonstrate that the performance of the HVDC System with respect to basic operating modes and continuous ratings are in conformance with the Specification and are not less than the levels quoted by the Contractor in his bid. | Bidder understands that HVDC Contractor shall be responsible for carrying out field tests post-refurbishment to verify the rated & overload capacities specified in TS clause 2.2.1 for both directions of power flow. | Bidder's understanding is in line with TS requirement.
60 | Chapter-11 |  | 11.12.3 |  | The thyristor failure rate shall be monitored over a period of 12 months starting at the end of six months following trial operation of the HVDC system. If the average failure rate of thyristors, over a period of these 12 months proves to be within the guaranteed value the guarantee shall be considered as fulfilled otherwise the guarantee period shall be extended by six (06) months. If the average failure rate of thyristors at the end of the extended period, the one year average number of occurrences/6 months, disregarding any six consecutive months with the highest thyristor failure rate is equal to or lower than the guaranteed value then the thyristor failure rate guarantee is considered to be fulfilled.. | There are contradictions within the clause. Bidder understands that the performance monitoring shall be done on per block basis in periods of six months each. Hence, Employer is requested to modify the clause as follows: "The thyristor failure rate shall be monitored over a two consecutive periods of 6 12 months each, starting at the end of six months following trial operation of the HVDC system. If the average failure rate of thyristors, over a period of these 6 12 months in both consecutive periods proves to be within the guaranteed value the guarantee shall be considered as fulfilled otherwise the guarantee period shall be extended by six (06) months. If the average failure rate of thyristors (averaged over six months per period) at the end of the extended period, during any two out of three periods of the one year six months each average number of occurrences/6 months, disregarding any period of six consecutive months with the highest thyristor failure rate is equal to or lower than the guaranteed value then the thyristor failure rate guarantee is considered to be fulfilled." | Please refer Amendment-1 .
61 | Chapter-11 |  | 11.13 |  | The relay module / C&P module / Component failure rate shall be monitored on per block basis over a period of six months starting at the end of six months after trial operation of HVDC system. If the failure rate of each type of relay module / C&P module / component averaged during these twelve months proves to be within the specified value, the guarantee shall be considered as fulfilled otherwise the guaranteed period shall be extended by six months. | Bidder understands that the performance monitoring shall be done on per block basis in periods of six months each. Hence, Employer is requested to modify the clause as follows: "The relay module / C&P module / Component failure rate shall be monitored on per block basis over a two consecutive periods of six months each, starting at the end of six months after trial operation of HVDC system. If the failure rate of each type of relay module / C&P module / component averaged during these two consecutive periods of six twelve months each proves to be within the specified value, the guarantee shall be considered as fulfilled otherwise the guaranteed period shall be extended by six months." | Please refer Amendment-1 .
66 | Vol-I/ Section-V/ SCC |  | Sr No-48 of SCC |  | Replacing Sub-Clause GCC 22.8.1 with the following: At the end of the Defect Liability Period, the Contractor's Liability ceases except for latent defects. The Contractor's liability for latent defects warranty shall be limited to period of ten (10) years from the end of Defect Liability Period. Latent defects are such defects for which it is established by the Employer that the defect was discovered/noticed after the date of expiration of the Defect Liability Period.................... The provisions contained in the clause will not be applicable: (a) If the Employer has not operated the equipment according to generally approved industrial practices and in accordance with the conditions of operation specified in the Contract by the Contractor and in accordance with operating manuals, if any. (b) In case of normal wear and tear normally applicable to equipment of the type supplied as determined by the Employer. Further, it will not apply to consumables and wearing parts. | We propose that latent defects warranty shall be limited to period of Five(5) years from the end of Defect Liability Period. Kindly accept | Please refer Amendment-1 .
67 | Vol-II/Part-1 |  | Chapter-11- 11.8 AVAILABILITY REQUIREMENT |  | REQUIREMENTS The calculated energy availability (EA) of each block (Block I & II) considered on a Six (consecutive) months basis and based on the Contractor's availability spare parts/equipment shall be equal to or shall exceed the specified value given below. Also, subject to the terms and conditions specified, the availability per year, considering forced outages, shall be equal to or exceed the guaranteed value. The Guaranteed Minimum Energy Availability Requirement (EA) of each HVDC block shall not be less than 99.8 % . The design target shall be 99.9 %. | Proposed Changes REQUIREMENTS The calculated energy availability (EA) of each block (Block I & II) considered on a Six (consecutive) months basis and based on the Contractor's availability spare parts/equipment shall be equal to or shall exceed the specified value given below. Also, subject to the terms and conditions specified, the availability per year, considering forced outages,shall be equal to or exceed the guaranteed value. The Guaranteed Minimum Energy Availability Requirement (EA) of each HVDC block shall not be less than 97% . The design target shall be 99.9 %. | Provision of bidding document shall prevail.
68 | Vol-II/Part-1 |  | Chapter-11- 11.8.2 FULFILLMENT OF AVAILABILITY GUARANTEE |  | Liquidated damages = Rs. 30 Million for each 0.1 % or part thereof for the shortfall below 99.8% down to 98 ( each block) (d) In case average annual energy availability as described in Para (c) above, is found to be below 98% the system (under present scope) shall be rejected by employer. The system rejection shall be governed as per provision of contract. | Proposed Changes Liquidated damages = Rs. 30 Million for each 0.1 % or part thereof for the shortfall below 97% down to 96% (d) In case average annual energy availability as described in Para (c) above, is found to be below 96% the contractor shall correct the necessary deficiencies and defects so that the annual energy availability averaged over the half year period period (excluding the previous period in Para (a), (b) and (c) above and the period for correcting such deficiencies) reaches 97%. | Provision of bidding document shall prevail.
69 | Vol-II/Part-1 |  | Chapter-11- 11.9.2 FULFILLMENT OF REALIABILITY GUARANTEE |  | c) After correction of such deficiencies and defects, if the number of occurrences/6months over a further half year period (excluding the previous one and half year period and the period for correcting such deficiencies) is still above the guaranteed value, liquidated damages calculated as per the formula below shall be paid by the Contractor to the Employer: = Rs. 1 Million for each EOF or part thereof above the guaranteed value. = Rs. 0.5 Million for each transient disturbance or part thereof above the guaranteed value | Proposed Changes c) After correction of such deficiencies and defects, if the number of occurrences/6months over a further half year period (excluding the previous one and half year period and the period for correcting such deficiencies) is still above the guaranteed value, liquidated damages calculated as per the formula below shall be paid by the Contractor to the Employer: = Rs. 0.5 Million for each EOF or part thereof above the guaranteed value. = Rs. 0.25 Million for each transient disturbance or part thereof above the guaranteed value | Provision of bidding document shall prevail.
70 | Vol-II/Part-1 |  | 11.11 STATION POWER RATING GUARANTEE |  | Maximum limit on compensation payable under (a) and (b) above in aggregate shall be 500 Million INR per block. However if the station rating is less than 98 % of rated continuous power, plant rejection as per the Provision of contract shall be applicable | In case, max cap of LD on a/c of performance guarantee is reached, there shall not be any rejection of the system and payment of such LDs shall completely satisfy the Contractor’s guarantees under GCC Sub-Clause 23.3, and the Contractor shall have no further liability whatsoever to the Employer in respect thereof. | Provision of bidding document shall prevail.
71 | Vol-II/Part-1 |  | 11.13 |  | 11.13 GUARANTEED FAILURE RATE OF RELAY MODULE/C&P MODULE/COMPONENT | We understand the relay module/C&P module shall be limited to HVDC controls only. Kindly confirm | The guaranteed failure rate requirement is applicable for RELAY MODULE/C&P MODULE/COMPONENT under the present scope.
72 | Vol-I/Part-1 |  | ITB 2.1 |  | Presently, the local content requirement to categorize a supplier as ‘Class-I local supplier’ is minimum 25%. | Since the refurbishment scope is very limited in nature and main equipments like valves & controls shall be supplied from offshore, we request to amend the requirement as "local content requirement exlcuding HVDC system shall be minimum 25%". | Provision of bidding document shall prevail.
73 | Vol II Chapter-1 |  | General: Control system | 1.2.xi | Existing C&P cubicles for the above shall be completely dismantled and stored at site. | The client specification requests for the dismantling of all AC control & protection cubicles. Please confirm if the entire HVAC substation control and protection system of the 400kV Chandrapur AC substation, including the one-and-a-half dia CB scheme, AC filter bays, converter transformer bay, 400kV line bay, and NGR bay, needs to be completely replaced and a new 'digital control system' needs to be provided. | Replacement of Control and protection of entire Chandrapur AC sub station is not in the scope. Only the AC C&P portion for bay/bus covered under TS Cl 1.2.xi are under present scope and existing C&P panels for only them are to be dismantled.
74 | Vol II Chapter-4 |  | 4.8 | 4.8.1 | The asynchronous data interface is required for communication between Remote Terminal Units (RTU) to be located at Chandrapur to Southern Regional Load Dispatch Centre (SRLDC). There shall be two nos. asynchronous data channels (i.e. one main channel and one stand-by channel) between RTU and the respective LDC. The asynchronous data channels shall be compatible with V.24/V.28 as per CCITT. | We envisage communication to load dispatch centers through gateways. Kindly confirm if an RTU needs to be provided for SRLDC communication. Are there any specific make and model require for the RTU? Could you also eleborate the required standard "V.24/V.28 as per CCITT" for communication to SRLDC? | Supply of applicable RTU along with all accessories shall be of Employer approved make. V.24/V.28 are well known Industry standard communication Interfaces.
75 | Annexure-NTAMC Remote Operation |  |  |  | Scope of work for Integration of HVDC Station with NTAMC/RLDC Control Centers: | We understand that scope is limited up to Gateway only, which to be provided at Chandrapur HVDC station in present Scope. No work is involved at NTAMC/RLDC end. Kindly confirm. | Bidder's understanding is correct.
76 | Chapter-1 of TS |  | 1.2 | 1 | Scope for AC control and protection system for AC Yard is as follows: Converter transformer. | Kindly share the type of Protection required for Converter transformers.If existing drgs are available, please share the same. Please also clarify the requirement of PQM and PMU for the converter transformer bays. | Protection requirement of Converter transfomers are detailed in Chapter-4 of TS
77 | Chapter-1 of TS |  | 1.2 | 4 | Scope for AC control and protection system for AC Yard is as follows: AC filter sub bank bays for each Pole and each side. | Kindly share the type of Protection required for AC Filter sub bank. If existing drgs are available please share the same. | Protection requirement of AC Filters are detailed in Chapter-4 of TS
78 | Chapter-1 of TS |  | 1.2 | 4 | Scope for AC control and protection system for AC Yard is as follows: AC filter sub bank bays for each Pole and each side. | Please clarify the requirement of detuning protection function for the Filter sub bank. | Protection requirement of AC Filters are detailed in Chapter-4 of TS
79 | Chapter-1 of TS |  | 1.2 |  | General | We understand that PMU integaration at PDC end shall not be a part of bidder scope. Please confirm. | PMU integration is not part of the scope
80 | Chapter 1 |  | 1.3.1 - C Studies for deciding the operational logic. |  | The operational logics refer to the specific operational guidelines and/or restrictions, which shall be required to be imposed on the HVDC system operation if it is to operate in an environment for which it has not been designed. This environment could exist because of the factors beyond the control of the Employer but in which the HVDC system being in operation becomes useful. The Employer then needs to know the limitations of the HVDC system. These environmental conditions could be characterised by factors like wide variation in voltage, frequency, temperature, pollution levels, humidity etc. | We request to kindly delete this clause as the equipment will be designed based upon the supplied Reference Design upon data contained in the technical Specifications about the environmental conditions variation in voltage, frequency, temperature, pollution levels, humidity etc. In addition the design will be based upon study results thereof which will be based on the Design Upon Data provided by the Employer. Therefore any limitations/restrictions which may be imposed to operation due to undefined conditions at this stage, will only be applicable when those changes in the Reference Data conditions are quantified and a new assessment done. | TS requirement shall be fulfilled
81 | Chapter 1 |  | 1.3.2 - C Studies for deciding the operational logic. |  | The surface / subsurface data given in Chapter 2 are only indicative. The Contractor shall be fully responsible for all surface and subsurface investigations required to establish foundation criteria and parameters for all site buildings and structures, as applicable. Bidder shall carry out soil investigation for outdoor cooler area and storage area before submission of bid. | We request Powergrid to provided assessment of the earthing mat and earthing points resistance measurements report | As per provsion of Bidding documents. Bidder is required to get acquainted with site condition. Further information may be shared during detailed engineering.
82 | Chapter 1 |  | 1.4.4.2 INTERFACE WITH EMPLOYER’S SERVICES |  | 13. Protection Interface- The contractor shall utilise existing CT/CVT inputs from HVDC West side AC Switchyard to Employer’s old 400 kV switchyard control room and vice versa for use in bus bar differential protections. Necessary arrangement shall be made by the Contractor to integrate these signals in the protection schemes as required. | We request Powergrid to provide detailed specification of the instrument transformers currently employed, as well as their latest maintenance reports. | Please refer appropriate Annexures to TS. For More information , Bidder may get in touch with site after award.
83 | Chapter 1 |  | 1.4.5 PERFORMANCE GUARANTEES |  | The Contractor shall design the HVDC system equipment under present scope in such a way that the performance parameters are met for all specified operating conditions and necessary measurements shall be made at the BTB station to prove conformance. If any deficiency is found, the Contractor shall carry out all modifications/ rectifications/ replacements required to meet the required performance, unless specified otherwise, at no extra cost to the Employer. All specified requirements must be fulfilled by the Contractor prior to the Employer accepting the Works or any part thereof. | Please amend as following; The Contractor shall design the HVDC system equipment under present scope in such a way that the performance parameters are met for all specified operating conditions and necessary measurements shall be made at the BTB station to prove conformance. If any deficiency related to the Contractor's scope of works is found, the Contractor shall carry out all modifications/ rectifications/ replacements required to meet the required performance, unless specified otherwise, at no extra cost to the Employer. All specified requirements must be fulfilled by the Contractor prior to the Employer accepting the Works or any part thereof. | Bidder's scope is limited to the provision of bidding documents.
84 | Chapter 1 |  | 1.5 EQUIPMENT MATERIALS AND SERVICES SUPPLIED BY THE EMPLOYER |  | The supply of all equipment, materials, and services required for the execution of the Works shall be the responsibility of the Contractor with the specific exception of the items listed herein. a) Converter Station Site | Please amend as following; The supply of all equipment, materials, and services required for the execution of the Works shall be the responsibility of the Contractor with the specific exception of the items listed herein. a) Converter Station Site with existing equipment in good coondition to provide continued safe and reliable service under use. | Bhadrawati HVDC station is presently under operation at its rated capacity. Bidder may visit the site to get acqainted with the detailed status of the equipment.
85 | Chapter 11 |  | 11.10.1.1 No Load Losses (Block wise) |  | These are the losses when the HVDC converter station is energized but with the converters blocked and all auxiliary equipments corresponding to immediate start up power connected with at least one cooling group of transformer, valve cooling system and valve hall ventilation system in service. No load loss shall be guaranteed corresponding to converter transformer set at principal tap with nominal ac system voltage (400 KV Both Side at 50 Hz) and at 400 C ambient temperature and 50 % ambient humidity level. Principal tap is the Tap Position of converter transformer when HVDC converter shall be delivering 1 p.u. power (500MW) at nominal DC voltage at rectifier, keeping AC system voltage 400 KV (Western Side) and 400KV (Southern Side), at 50 Hz and 400 C ambient Temperature for Pole 1 /2 | Converter transformer and HVAC system for Valve hall is out of scope therefore "no load" loss calculation will be including the valve cooling loss data only. Please confirm. | Confirmed that Converter transformer and HVAC system are not under present scope and hence not included under loss calculation.Methodology for calculation of losses is clearly explained in TS Cl 11.10.2
86 | Chapter 2 |  | 2.2.1 OVERVIEW |  | The scheme must also operate for five seconds at power transfer up to 2x600MW (1.2pu power transmission, 1200MW; with all redundant coolers and heat exchangers out of service and maximum ambient temperature. | Please amend as following; The scheme must also operate for five seconds at power transfer up to 2x600MW (1.2pu power transmission, 1200MW; with all redundant coolers and heat exchangers in service and maximum ambient temperature. | Provision of bidding document shall prevail.
87 | Chapter 2 |  | 2.2.1 OVERVIEW |  | Valve Hall Temperature 10͘ °C to 55͘ °C, and maximum relative air humidity in the valve hall is 60% | Since HVAC system for Valve Hall is out of supplier scope, we request Powergrid to ensure that the HVAC will keep the valve hall at the specified temperatures and humidity up to and including maximum/minimum prevailing ambient temperatures. | Please refer Chapter 7.4 alongwith chapter 2.2.1 for HVAC and ventilation requirements of valve hall
88 | PART-1 Chapter-7 |  | 7.3.3.8. Design Cooling Requirements |  | Cooling system shall be capable to operate and guarantee the design temperature range of cooling water for two hours and five seconds overload conditions, up to max specified design dry bulb ambient temperature. | Please clarify what are the overload conditions and the reason of this requirement | Kindly refer Chapter-2 for Overload conditions.
89 | PART-1 Chapter-7 |  | 7.3.3.15. Leakage Detection |  | There shall be three leakage detection methods used in parallel by the cooling control system. These methods can, depending on the nature of the leakage, generate trip of the SECTION-7 converter and cooling system. | We normally monitor the leakages by means of expansion level, which is sufficient. We also monitor the level under the pumps trays to detect possible leakage from the pumps. Please confirm that this is sufficient to monitor leakages | Noted
90 | PART-1 Chapter-7 |  | 7.3.2.b. |  | Cooling towers shall be dry type for fine water system. | Please clarify meaning of "cooling towers" does it mean dry blast air coolers? | Cooling tower refers to coolers on foundation and all related accessories.
91 | Chapter 1 |  |  | 1.4.4.2 INTERFACE WITH EMPLOYER SERVICE 1.SITE AUXILIARIES | Station Supply is existing from tertiary of ICT and additionally 33 kV feeder from state electricity board. The existing auxillary supply and existing cabling from ACDB and DCDB shall be used | The LT SLD given in Annexure-C is having only 11KV System hence please confirm acctual rating of MV system which drives the 415V LT System. Request to please provide the overall complete SLD of LT System having details of all LT boards (ACDB,DCDB,UPS). | LT SLD is correct. 11kV board feeds the 11/0.4kV transformer. 11kV board is fed from 33kV source through separate 33/11kV transformer.
92 | Chapter 1 |  |  | 1.2 SCOPE OF WORK e) Integration Scope | In case the existing SCADA UPS system does not have the sufficient capacity for the HMI system to be supplied under present scope, the contractor needs to supply redundant UPS System for additional capacity (the backup time shall be 30 minutes and requirement of single phase/ three phase shall be decided during the detailed engineering). | Please provide the rating of the existing station UPS and incase extension of the same is required then the new ups & batteries location to be confirmed. | Rating and loading details of the existing UPS are already provided in TS. Location of new UPS if required may be placed in AC Equipment Room in the Ground Floor.
93 | Chapter 1 |  |  | Annexure-Z ,Battery Details |  | Please confirm if Battery replacment is required ,If yes please confirm whether we can consider Ni-Cad batteries for 220V & 48V DC System. | Battery replacement is in the present scope as per TS. Details of type of battery to be supplied is covered in Annexure-Z.
94 | Chapter 1 |  |  | Annexure-Z ,Price Bid | DC system shall consist of 1 set of battery bank, 1 set of battery charger complete with DC distribution board for each of 220V & 48V systems respectively. | Please share the existing DC SLD. | Refer 'Annexure-A- ACDB and DCDB Distribution Details' of TS.
95 | Chapter 1 |  |  | Annexure B Valve Hall Layout and Section |  | Please furnish the detailed section for valve hall & converter transformer showing elevation of wall bushing for layout preparation. | Refer 'Annexure B Valve Hall Layout and Section' is provided. Further, the Bidder may visit site to collect further details.
96 | Chapter 1 |  |  | Annexure B Control room layout_GF |  | Please provide the sizes of Battery room, AC equipment 1 & 2 and DC distribution 1 &2. | Refer 'Annex-A-Service Building Layout_GF'.Bidder may visit the site to acquaint better with such details.
97 | Chapter 1 |  |  | 1.2 SCOPE OF WORK 1.SITE AUXILIARIES 3. Earthing Connections: | Earthing of panels and additional equipment and structures under the present scope is in the scope of the contractor. | We understand that only above ground earthing for newly supplied structure /equipment will be in present scope and existing earthing can also be utilized. | Bidder's understanding is inline with TS.
98 | Chapter 6 |  |  | 6.3 SURGE ARRESTERS |  | Please provide the existing DC surge arester rating & other details. | Refer 'Annexure A AC Surge Arresters Ratings' of TS which also includes details of DC surge arresters.
99 | Chapter 6 |  |  | 6.18.1 Lighting System | Lighting System shall be as per Annexure-Lighting System for present scope of work (i.e Store and Battery Room) | We understand that Lighting work will be done only for store & battery room. | Bidder's understanding is inline with TS.
100 |  |  |  | General | Powe & Control Cables | Based on site visit, it is suggested to replace all the cables related to new supplies as existing cables are more than 25yrs old and hence system performance cant be guranteed with them. Please amend the scope accordingly | Replacement af Power & Control cables for the present scope of work shall be done as per provision of TS.
101 | ITB 2.1 in BDS, Section-III, Vol-I |  |  |  | This Invitation for Bids, issued by the Employer is open to all firms including company(ies), Government owned Enterprises registered and incorporated in India as per Companies Act, 1956, barring Government Department as well as foreign bidders/MNCs not registered and incorporated in India and those bidders with whom business is banned by the Employer. | The provisions of this clause contradict Cl. 1.9 under Chapter-1 of TS: "In case, the bidder is a foreign entity submitting its bid as an individual Firm or in a Joint Venture without any Indian Entity as a partner, he, however, has the option, to be exercised as a part of his bid proposal, to propose an Associate(s) to execute the Second and/or Third Contract." We understand that the provisions of Cl. 1.9 & 1.10 under Chapter-1 of TS will prevail over BDS 3 (ITB 2.1). Employer is requested to confirm Bidder's understanding. | Please refer Amendment No-I.
102 | Appendix–2 (Price Adjustment) of Section-VI/ Forms & Proceedures, Vol-I |  |  |  | Ex-works Price Component:- The formula for calculating the price adjustment to be applied to the Ex-works price component for the equipment/materials will be as follows: dEC = EC0x {0.15 + a x (A1 /A0) + b x (B1 /B0) + c x (C1 /C0) + d x ( D1 /D0) + …….. + l x (L1 /L0) } - EC0 dEC= Price adjustment amount, expressed in currency of bid, payable to Contractor, for each shipment (if it works out negative, that would mean the amount to be recovered by the Employer from the Contractor). EC0= Ex-works price of the equipment in the currency of the bid, shipment wise. A,B,C, D, E etc. = Corresponding published recognized price indices for various materials used in the equipment L= Indian field labour index – namely All India Average Consumer Price Index Numbers for Industrial Workers (monthly) (Base: 2016= 100), as published by Labour Bureau, Shimla, Government of India (www.labourbureaunew.gov.in) a,b,c = Co-efficients (expressed as component of bid Price) of major d,e etc. materials involved in the Ex-works price of the equipment. The coefficients are estimated percentage of major raw material component involved in the Price of the equipment the sum of these coefficients shall be between 0.50 and 0.60. l = Coefficient of labour, value of which shall be between 0.25 and 0.35 2.1 i) Subscript '0' refers to indices as on thirty (30) days prior to date of opening of Bids, for materials & labour. ii) Subscript '1' refers to indices as applicable on: a) Sixty (60) days prior to the date of shipment for Labour. b) At the expiry of two third (2/3) period from the date of base index to the shipment of material. 2.2 The total adjustment for Ex-Works price component of the equipment (excluding equipment and consumable materials required for erection and recommended spares), shall not be subject to any ceiling whatsoever. | In line with other 'Domestic Bidding' We Propose 'Price Adjustment' for Major Equipment’s to be governed by Below formulas only:- PVC/XLPE Insulated Power and Control Cables P1 = P0 x {0.85 + 0.15 x (A1/A0)} – P0 + (M1 – M0) Where, P1 = Price adjustment amount per Km. of cable. Po = Ex-works price per Km. of cable. A = Price index for PVC/XLPE as published by IEEMA. M1 – M0 = Change in metal component of the ex-works price of particular type & size of cable. Where, M = Weight in MT of metal per Km. of Cable x Price index of metal per MT as published by IEEMA. The Bidder has to specify in his Bid metal component per Km. for each type and size of cable. Sub Station Structures (including Bolts & Nuts) For Lattice & Pipe Structures (including washers, foundation bolts and Bolts & Nuts). P1 = P0 x {0.15 + 0.58 x (A1/A0) + 0.16 (B1/B0) + 0.11 (L1/L0)} – P0 Where, P1 = Price adjustment amount shipment-wise. P0 = Ex-works price of Lattice & Pipe Type Structure including washers, foundation bolts, bolts & nuts. A = Average JPC Market Price (Retail) of Steel Structure of Steel Angles of size 50 x 50 x 6 mm in Rupees per MT as published by Joint Plant Committee (JPC) [constituted by GOI] for all cities i.e. Kolkata, Delhi, Mumbai & Chennai inclusive of GST component (www.jpcindiansteel.nic.in) B = Price indices of electrolytic zinc as published by IEEMA. L = Indian field labour index – namely All India average consumer price index for Industrial Workers (monthly) (Base: 2016= 100), as published by Labour Bureau, Shimla, Government of India (http://labourbureaunew.gov.in). 2.1.1 i) Subscript '0' refers to indices as on thirty (30) days prior to date of opening of Bids, for materials & labour. ii) Subscript '1' refers to indices and exchange rate as applicable on: a) Sixty (60) days prior to the date of shipment for Labour. b) At the expiry of two third (2/3) period from the date of base index to the date of shipment for materials in case of SA. c) Sixty (60) days prior to the date of shipment for materials in case of Power & Control Cables and Sub-station structure. | Provision of the Bidding Document shall remain unchanged.
103
104 | [5 empty] | We presume 'Price Adjustment' should also be applicable for the items to be sourced from off-shore country & relevant 'Indices' shall be proposed by the Bidder during Bid Submission. Kindly confirm | Provision of Bidding Documents are amply clear in this regard, further, it is requested to refer Cl. 5(b), Appendix-2 (Price Adjustment), Section-VI, which states that "In case IEEMA does not publish any of the price indices, as mentioned above, the Bidder shall indicate any nationally recognised published index for respective items and the source of the same shall be furnished in the Bid."
105 | GCC 23.2 in SCC, Section-V, Vol-I |  |  |  | 23. Functional Guarantees 23.1 The Contractor guarantees that the Facilities and all parts thereof shall attain the Functional Guarantees specified in the Technical Specifications, subject to and upon the conditions therein specified. 23.2 If, for reasons attributable to the Contractor, the minimum level of the Functional Guarantees specified in the Technical Specifications are not met either in whole or in part, the Contractor shall at its cost and expense make such changes, modifications and/or additions to the Plant or any part thereof as may be necessary to meet at least the minimum level of such Guarantees. The Contractor shall notify the Employer upon completion of the necessary changes, modifications and / or additions, and shall request the Employer to repeat the Guarantee Test until the minimum level of the Guarantees has been met. If the Contractor eventually fails to meet the minimum level of Functional Guarantees, the Employer may consider termination of the Contract, pursuant to GCC Sub-Clause 36.2.2 and the Contractor shall be liable for the amount already paid by the Employer for the Facilities or its part thereof. .............................................. | Referring to the clause of SCC- which states that ' In case of failure to meet the minimum functional guarantee' Contractor shall be liable for the amount already paid by the Employer for the Facilities or its part thereof. We propose as the Contractor is already being penalized through 'Liquidated Damage' on account of shortfall in PG parameters, no further penalty/deduction of any nature shall be applied by PGCIL. | Provision of the Bidding Document shall remain unchanged.
106 | GCC 22.8 in SCC, Section-V, Vol-I |  |  |  | 22. Defect Liability ..................................... GCC 22.8 If the Facilities or any part thereof cannot be used by reason of such defect and/or making good of such defect, the Defect Liability Period of the Facilities or such part, as the case may be, shall be extended by a period equal to the period during which the Facilities or such part cannot be used by the Employer because of any of the aforesaid reasons. Upon correction of the defects in the Facilities or any part thereof by repair/replacement, such repair/replacement shall have the Defect Liability Period extended by a period mentioned in GCC Sub-Clause 22.2 from the time of such replacement/repair of the facilities or any part thereof. However such extensions shall be limited up to period of 7 years of operation from the date of Taking Over/Completion of Facilities. ..................................... | We propose that such extensions shall be limited up to period of 4 years of operation from the date of Taking Over/Completion of Facilities. Kindly accept | Provision of the Bidding Document shall remain unchanged.
107 | GCC 22.8.1 in SCC, Section-V, Vol-I |  |  |  | GCC 22.8.1 At the end of the Defect Liability Period, the Contractor's Liability ceases except for latent defects. The Contractor's liability for latent defects warranty shall be limited to period of ten (10) years from the end of Defect Liability Period. Latent defects are such defects for which it is established by the Employer that the defect was discovered/noticed after the date of expiration of the Defect Liability Period, but was existing before the expiration of Defect Liability Period and the defects were lying within the material or arising out of design deficiency. Contractor’s liability shall be limited to repair and replacement of defective parts and shall cease upon end of ten years from the date of completion of Defect Liability Period or end of availability & reliability period whichever is later. The provisions contained in the clause will not be applicable: (a) If the Employer has not operated the equipment according to generally approved industrial practices and in accordance with the conditions of operation specified in the Contract by the Contractor and in accordance with operating manuals, if any. (b) In case of normal wear and tear normally applicable to equipment of the type supplied as determined by the Employer. Further, it will not apply to consumables and wearing parts. | We propose that latent defects warranty shall be limited to period of Five(5) years from the end of Defect Liability Period. Kindly accept | Please refer of Amendment No-I.
108 | ITB 2.1 in BDS, Section-III, Vol-I |  |  |  | ….................................. Further, the firm has to be a ‘Class-I local supplier’ as defined under Public Procurement (Preference to Make in India) Order, 2017 issued by Department for promotion of Industry and Internal Trade (DPIIT), Ministry of Commerce and Industry, Government of India vide order dated 15/06/2017, its revision dated 16/09/2020 (PPP-MII Order) read in conjunction with ‘Public Procurement (Preference to Make in India) to provide for Purchase Preference (linked with local content) in respect of Power Sector’ order dated 16/11/2021 issued by Ministry of Power (MoP Order) and subsequent modifications/ amendments if any Presently, the local content requirement to categorize a supplier as ‘Class-I local supplier’ is minimum 25%. Firms who are not ‘Class-I local supplier‘ shall not be eligible to bid. ......................................... | Since the refurbishment scope is very limited in nature and main equipments like valves & controls shall be supplied from offshore, we request to amend the requirement as "local content requirement exlcuding HVDC system shall be minimum 25%". | Provision of the Bidding Document shall remain unchanged.
109 | GCC 1.1 (n) & 4.1, Section-IV, Vol-I |  |  |  | 1.1 (n) “Effective Date” means the date of Notification of Award from which the Time for Completion shall be determined 4. Time for Commencement and Completion 4.1 The Contractor shall commence work on the Facilities from the Effective Date of Contract and without prejudice to GCC Sub-Clause 21.2 hereof, the Contractor shall thereafter proceed with the Facilities in accordance with the time schedule specified in the corresponding Appendix – 4 (Time Schedule) to the Contract Agreement. ................................ | We request to modify the definition of "Effective Date" as under: "Effective Date” means the date of Notification of Award from which the Time for Completion shall be determined. Further, time for completion shall be measured from commencement date which is defined as below : "Commencement Date" means the date of fulfilment of all conditions stated below: (a) This Contract Agreement has been duly executed for and on behalf of the Employer and the Contractor. (b) The Employer has paid the Contractor the advance payment within 15 days of receipt of eqvt. advance bank guarantee (ABG) & contract performance bank guarantee (CPBG) from contractor. The Contractor shall submit the ABG & CPBG within 15 days from date of NoA/LoA. Sub Clause 4.1 : The Contractor shall commence work on the Facilities from the Effective Date Commencement Date of Contract and without prejudice to GCC Sub-Clause 21.2 hereof, the Contractor shall thereafter proceed with the Facilities in accordance with the time schedule specified in the corresponding Appendix – 4 (Time Schedule) to the Contract Agreement. | Provision of the Bidding Document shall remain unchanged.
110 | GCC 34.1, Section-IV, Vol-I |  |  |  | 34. Extension of Time for Completion 34.1 The Time(s) for Completion specified in the SCC shall be extended if the Contractor is delayed or impeded in the performance of any of its obligations under the Contract by reason of any of the following: (a) any Change in the Facilities as provided in GCC Clause 33 (b) any occurrence of Force Majeure as provided in GCC Clause 32 (c) any suspension order given by the Employer under GCC Clause 35 hereof or reduction in the rate of progress pursuant to GCC Sub-Clause 35.2 or (d) any changes in laws and regulations as provided in GCC Clause 31 or (e) any other matter specifically mentioned in the Contractby such period as shall be fair and reasonable in all the circumstances and as shall fairly reflect the delay or impediment sustained by the Contractor. | We request to modify the said clause as under : The Time(s) and cost for Completion specified in the SCC shall be extended if the Contractor is delayed or impeded in the performance of any of its obligations under the Contract by reason of any of the following: (a) any Change in the Facilities as provided in GCC Clause 33 (b) any occurrence of Force Majeure as provided in GCC Clause 32 (c) any suspension order given by the Employer under GCC Clause 35 hereof or reduction in the rate of progress pursuant to GCC Sub-Clause 35.2 or suspension by the Contractor under new Clause proposed. (d) any changes in laws and regulations as provided in GCC Clause 31 or (e) any other matter specifically mentioned in the Contract, or (f) any delay or default on the part of the Employer or its other contractors in fulfilling its obligations under the Contract, by such period and amount as shall be fair and reasonable in all the circumstances and as shall fairly reflect the delay or impediment sustained by the Contractor. | Provision of the Bidding Document shall remain unchanged.
111 | GCC 35, Section-IV, Vol-I |  |  |  | GCC 35 Suspension 35.1 The Employer may request the Project Manager, by notice to the Contractor, to order the Contractor to suspend performance of any or all of its obligations under the Contract. Such notice shall specify the obligation of which performance is to be suspended, the effective date of the suspension and the reasons therefor. The Contractor shall thereupon suspend performance of such obligation (except those obligations necessary for the care or preservation of the Facilities) until ordered in writing to resume such performance by the Project Manager. …………….……………………….. | We request to modify the said clause as under : (a) Contract Price properly attributable to the parts of the Facilities executed as on the date of termination including items supplied, products under manufacturing, products ready for inspection or dispatch, products dispatched, services completed or under construction for this contract; (b) any amount paid to subcontractors towards termination of sub-contracts including cancellation charges (c) the costs reasonably incurred by the Contractor in the removal of the Contractor's Equipment from the Site and in the repatriation of the Contractor's and its Subcontractor's personnel (d) costs incurred by the Contractor in protecting the Facilities and leaving the Site in a clean and safe condition (e) the cost of satisfying all other obligations, commitments and claims that the Contractor may in good faith have undertaken with third parties in connection with the Contract and that are not covered by paragraphs (a) through (d) above. | Provision of the Bidding Document shall remain unchanged.
112 | GCC 36, Section-IV, Vol-I |  |  |  | GCC 36. Termination 36.1 Termination for Employer‟s Convenience 36.1.1 The Employer may at any time terminate the Contract for any reason by giving the Contractor a notice of termination that refers to this GCC Sub-Clause 36.1. ………………… ……………………………….. 36.2 Termination for Contractor‟s Default 36.2.1 The Employer, without prejudice to any other rights or remedies it may possess, may terminate the Contract forthwith in the following circumstances by giving a notice of termination and its reasons therefor to the Contractor, referring to this GCC Sub-Clause 36.2: …………….. …………………………………. | We request to kindly add the following under the provisions of Clause 36: 36A 1: The Contractor may by giving 30 days notice to the Owner, terminate the Contract under the following circumstances: (a) If the Owner: (i) has failed to pay the Contractor the amounts specified in any undisputed invoice, in whole or in part, as may have been invoiced by the Contractor in accordance with the terms and conditions of the Contract or delays in issuing payment security or the Owner (and/or its other contractors ) has defaulted in performaing any of its other obligations in terms of this Contract and the Owner has failed to remedy its default including its payment default within 45 days after the receipt of the Contractor's notice requiring the Owner to remedy such default, or (ii) becomes bankrupt or insolvent... undertaking or assets. 36A 2: In the event of termination of the Contract by the Contractor in terms of Clause 36A 1, the Contractor shall be entitled to payment in accordance with Clause 36.1.3. | Provision of the Bidding Document shall remain unchanged.
113 | GCC 36.1.3, Section-IV, Vol-I |  |  |  | GCC 36. Termination ….............................. 36.1.3 In the event of termination of the Contract under GCC Sub-Clause 36.1.1, the Employer shall pay to the Contractor the following amounts: (a) the Contract Price, properly attributable to the parts of the Facilities executed by the Contractor as of the date of termination (b) the costs reasonably incurred by the Contractor in the removal of the Contractor‟s Equipment from the Site and in the repatriation of the Contractor‟s and its Subcontractors‟ personnel (c) any amounts to be paid by the Contractor to its Subcontractors in connection with the termination of any subcontracts, including any cancellation charges (d) costs incurred by the Contractor in protecting the Facilities and leaving the Site in a clean and safe condition pursuant to paragraph (a) of GCC Sub-Clause 36.1.2 (e) the cost of satisfying all other obligations, commitments and claims that the Contractor may in good faith have undertaken with third parties in connection with the Contract and that are not covered by paragraphs (a) through (d) above. | We request to modify the said clause as under : (a) Contract Price properly attributable to the parts of the Facilities executed as on the date of termination including items supplied, products under manufacturing, products ready for inspection or dispatch, products dispatched, services completed or under construction for this contract; (b) any amount paid to subcontractors towards termination of sub-contracts including cancellation charges (c) the costs reasonably incurred by the Contractor in the removal of the Contractor's Equipment from the Site and in the repatriation of the Contractor's and its Subcontractor's personnel (d) costs incurred by the Contractor in protecting the Facilities and leaving the Site in a clean and safe condition (e) the cost of satisfying all other obligations, commitments and claims that the Contractor may in good faith have undertaken with third parties in connection with the Contract and that are not covered by paragraphs (a) through (d) above. | Provision of the Bidding Document shall remain unchanged.
114 | GCC 32.1, Section-IV, Vol-I |  |  |  | 32. Force Majeure 32.1 “Force Majeure” shall mean any event beyond the reasonable control of the Employer or of the Contractor, as the case may be, and which is unavoidable notwithstanding the reasonable care of the party affected, and shall include, without limitation, the following: (a) war, hostilities or warlike operations (whether war be declared or not), invasion, act of foreign enemy and civil war, (b) rebellion, revolution, insurrection, mutiny, usurpation of government, conspiracy, riot and civil commotion, (c) earthquake, landslide, volcanic activity, flood or cyclone, or other inclement weather condition, nuclear and pressure waves or other natural or physical disaster, | We request to modify the said clause as under : 32.1 “Force Majeure” shall mean any event beyond the reasonable control of the Employer or of the Contractor, as the case may be, and which is unavoidable notwithstanding the reasonable care of the party affected, and shall include, without limitation, the following: (a) war, hostilities or warlike operations (whether war be declared or not), invasion, act of foreign enemy and civil war, (b) rebellion, revolution, insurrection, mutiny, usurpation of government, conspiracy, riot and civil commotion, (c) earthquake, landslide, volcanic activity, flood or cyclone, or other inclement weather condition, nuclear and pressure waves or other natural or physical disaster, (d) Epidemic & Pandemic | Provision of the Bidding Document shall remain unchanged.
115 | GCC 32.4, Section-IV, Vol-I |  |  |  | 32. Force Majeure ................................... 32.4 The party who has given such notice shall be excused from the performance or punctual performance of its obligations under the Contract for so long as the relevant event of Force Majeure continues and to the extent that such party‟s performance is prevented, hindered or delayed. The Time for Completion shall be extended in accordance with GCC Clause 34. | We request you to please add the following as clause 32.5: If the performance of the Contract is substantially prevented, hindered or delayed owing to Force Majuere for a consecutive period of more than 90 days or an aggregate period of more than 120 days on account of one or more events of Force Majeure during the currency of the Contract the Contractor shall have the right to terminate either the affected portion of the Facilities or the Contract if the event affects the whole Contract. | Provision of the Bidding Document shall remain unchanged.
116 | [5 empty] | We request to modify the said clause as under : The party who has given such notice shall be excused from the performance or punctual performance of its obligations under the Contract for so long as the relevant event of Force Majeure continues and to the extent that such party‟s performance is prevented, hindered or delayed. The Time for Completion shall be extended in accordance with GCC Clause 34. Further, the Contractor will also be entitled to an equitable adjustment of the Contract Price. Further, the Employer recognizes that in case of epidemics or pandemics (or evolution of existing epidemics or pandemics), the precautionary, mitigation or corrective measures implemented by the Contractor in the frame of the Contract are implemented in the best interest of the Employer and the Contract performance, and the Employer and the Contractor both agree that the additional costs reasonably incurred by Contractor in implementing such measures shall be compensated by the Employer to the Contractor. | Provision of the Bidding Document shall remain unchanged.
117 | GCC 33.2.5 Section-IV, Vol-I |  |  |  | 33. Change in the Facilities 33.1 Introducing a Change 33.2.5 The Employer shall issue the Contractor with a Change Order pursuant to GCC Sub-Clause 33.2 by way of amendment to the Contract or in any other manner deemed appropriate. Even if the Employer and the Contractor cannot reach agreement on the price for the Change, an equitable adjustment to the Time for Completion, or any other matters related to the Change Proposal, the Employer may nevertheless instruct the Contractor to proceed with the Change by issue of a “Pending Agreement Change Order” (“Pending Agreement Amendment”). Upon receipt of a Pending Agreement Change Order, the Contractor shall immediately proceed with effecting the Changes covered by such Order. The parties shall thereafter attempt to reach agreement on the outstanding issues under the Change Proposal. If the parties cannot reach agreement within sixty (60) days from the date of issue of the Pending Agreement Change Order, then the matter may be referred to the Arbitrator in accordance with the provisions of GCC Clause 38 & 39. | We request to modify the said clause as under : The Employer shall issue the Contractor with a Change Orderpursuant to GCC Sub-Clause 33.2 by way of amendment to the Contract or in any other manner deemed appropriate. Even if the Employer and the Contractor cannot shall reach agreement on the price for the Change, an equitable adjustment to the Time for Completion, or any other matters related to the Change Proposal, before the the Employer may nevertheless instruct the Contractor to proceeds with the Change by issue of a “Pending Agreement Change Order” (“Pending Agreement Amendment”). Upon receipt of a Pending Agreement Change Order, the Contractor shall immediately proceed with effecting the Changes covered by such Order. The parties shall thereafter attempt to reach agreement on the outstanding issues under the Change Proposal If the parties cannot reach agreement within sixty (60) days from the date of issue of the Pending Agreement Change Order, then the matter may be referred to the Arbitrator in accordance with the provisions of GCC Clause 38 & 39. Futher, the Employer shall not require any Change in case of the following: (i) if the Change shall result in unforeseeable changes in relation to scope (ii) in case goods are not readily available, (iii) in case it has an impact on Guarantees, (iv) in case it has an impact on EHS or an impact on the Contract’s intended purpose. | Provision of the Bidding Document shall remain unchanged.
118 | Appendix-1 of Contract Agreement, Section-VI,Forms & Proceedures, Vol-I |  |  |  | 2. PAYMENT PROCEDURES 2.1 Method of Payment The Employer shall make payments promptly within thirty (30) days of submission of an invoice/claim by the Contractor, complete in all respects and supported by the requisite documents and fulfillment of stipulated conditions, if any. All the payment shall be released to the Contractor directly. All payments to be made directly to the Contractor shall be made by the Employer though electronic payment mechanism (e-payment) for which necessary details shall be tied up during execution of the Contract. However, a request for payment to be released through cheque shall be considered on case to case basis and merit of the same. | We request to modify the said clause as under : All payments to be made directly to the Contractor shall be made by the Employer though electronic payment mechanism (e-payment) irrevocable letter of credit for which necessary details shall be tied up during execution of the Contract. However, a request for payment to be released through cheque shall be considered on case to case basis and merit of the same. | Provision of the Bidding Document shall remain unchanged.

## Commercial (hidden)
Clarification No-I_Commercial dated xx.10.2024 to the bidding documents of Refurbishment of HVDC Control, Protection, SCADA, Valve Hall Equipment and Valve Cooling System for 2x500 MW Chandrapur HVDC Back to Back (BTB) Station under Add-Cap; Specification Number: CC/NT/W-HVDC/DOM/A00/24/12849
Sl. No. | Reference document/ Clause No. | EXISTING CLAUSE | QUERY DESCRIPTION | POWERGRID REPLY - CS | POWERGRID REPLY2
1 | ITB 2.1 in BDS, Section-III, Vol-I | This Invitation for Bids, issued by the Employer is open to all firms including company(ies), Government owned Enterprises registered and incorporated in India as per Companies Act, 1956, barring Government Department as well as foreign bidders/MNCs not registered and incorporated in India and those bidders with whom business is banned by the Employer. | The provisions of this clause contradict Cl. 1.9 under Chapter-1 of TS: "In case, the bidder is a foreign entity submitting its bid as an individual Firm or in a Joint Venture without any Indian Entity as a partner, he, however, has the option, to be exercised as a part of his bid proposal, to propose an Associate(s) to execute the Second and/or Third Contract." We understand that the provisions of Cl. 1.9 & 1.10 under Chapter-1 of TS will prevail over BDS 3 (ITB 2.1). Employer is requested to confirm Bidder's understanding. | Please refer Amendment No-I. | Suitable amendment may be issued
2 | Appendix–2 (Price Adjustment) of Section-VI/ Forms & Proceedures, Vol-I | Ex-works Price Component:- The formula for calculating the price adjustment to be applied to the Ex-works price component for the equipment/materials will be as follows: dEC = EC0x {0.15 + a x (A1 /A0) + b x (B1 /B0) + c x (C1 /C0) + d x ( D1 /D0) + …….. + l x (L1 /L0) } - EC0 dEC= Price adjustment amount, expressed in currency of bid, payable to Contractor, for each shipment (if it works out negative, that would mean the amount to be recovered by the Employer from the Contractor). EC0= Ex-works price of the equipment in the currency of the bid, shipment wise. A,B,C, D, E etc. = Corresponding published recognized price indices for various materials used in the equipment L= Indian field labour index – namely All India Average Consumer Price Index Numbers for Industrial Workers (monthly) (Base: 2016= 100), as published by Labour Bureau, Shimla, Government of India (www.labourbureaunew.gov.in) a,b,c = Co-efficients (expressed as component of bid Price) of major d,e etc. materials involved in the Ex-works price of the equipment. The coefficients are estimated percentage of major raw material component involved in the Price of the equipment the sum of these coefficients shall be between 0.50 and 0.60. l = Coefficient of labour, value of which shall be between 0.25 and 0.35 2.1 i) Subscript '0' refers to indices as on thirty (30) days prior to date of opening of Bids, for materials & labour. ii) Subscript '1' refers to indices as applicable on: a) Sixty (60) days prior to the date of shipment for Labour. b) At the expiry of two third (2/3) period from the date of base index to the shipment of material. 2.2 The total adjustment for Ex-Works price component of the equipment (excluding equipment and consumable materials required for erection and recommended spares), shall not be subject to any ceiling whatsoever. | In line with other 'Domestic Bidding' We Propose 'Price Adjustment' for Major Equipment’s to be governed by Below formulas only:- PVC/XLPE Insulated Power and Control Cables P1 = P0 x {0.85 + 0.15 x (A1/A0)} – P0 + (M1 – M0) Where, P1 = Price adjustment amount per Km. of cable. Po = Ex-works price per Km. of cable. A = Price index for PVC/XLPE as published by IEEMA. M1 – M0 = Change in metal component of the ex-works price of particular type & size of cable. Where, M = Weight in MT of metal per Km. of Cable x Price index of metal per MT as published by IEEMA. The Bidder has to specify in his Bid metal component per Km. for each type and size of cable. Sub Station Structures (including Bolts & Nuts) For Lattice & Pipe Structures (including washers, foundation bolts and Bolts & Nuts). P1 = P0 x {0.15 + 0.58 x (A1/A0) + 0.16 (B1/B0) + 0.11 (L1/L0)} – P0 Where, P1 = Price adjustment amount shipment-wise. P0 = Ex-works price of Lattice & Pipe Type Structure including washers, foundation bolts, bolts & nuts. A = Average JPC Market Price (Retail) of Steel Structure of Steel Angles of size 50 x 50 x 6 mm in Rupees per MT as published by Joint Plant Committee (JPC) [constituted by GOI] for all cities i.e. Kolkata, Delhi, Mumbai & Chennai inclusive of GST component (www.jpcindiansteel.nic.in) B = Price indices of electrolytic zinc as published by IEEMA. L = Indian field labour index – namely All India average consumer price index for Industrial Workers (monthly) (Base: 2016= 100), as published by Labour Bureau, Shimla, Government of India (http://labourbureaunew.gov.in). 2.1.1 i) Subscript '0' refers to indices as on thirty (30) days prior to date of opening of Bids, for materials & labour. ii) Subscript '1' refers to indices and exchange rate as applicable on: a) Sixty (60) days prior to the date of shipment for Labour. b) At the expiry of two third (2/3) period from the date of base index to the date of shipment for materials in case of SA. c) Sixty (60) days prior to the date of shipment for materials in case of Power & Control Cables and Sub-station structure. | Provision of the Bidding Document shall remain unchanged. | CS to reply
3 |  |  | We presume 'Price Adjustment' should also be applicable for the items to be sourced from off-shore country & relevant 'Indices' shall be proposed by the Bidder during Bid Submission. Kindly confirm | Provision of Bidding Documents are amply clear in this regard, further, it is requested to refer Cl. 5(b), Appendix-2 (Price Adjustment), Section-VI, which states that "In case IEEMA does not publish any of the price indices, as mentioned above, the Bidder shall indicate any nationally recognised published index for respective items and the source of the same shall be furnished in the Bid." | CS to reply
4 | GCC 23.2 in SCC, Section-V, Vol-I | 23. Functional Guarantees 23.1 The Contractor guarantees that the Facilities and all parts thereof shall attain the Functional Guarantees specified in the Technical Specifications, subject to and upon the conditions therein specified. 23.2 If, for reasons attributable to the Contractor, the minimum level of the Functional Guarantees specified in the Technical Specifications are not met either in whole or in part, the Contractor shall at its cost and expense make such changes, modifications and/or additions to the Plant or any part thereof as may be necessary to meet at least the minimum level of such Guarantees. The Contractor shall notify the Employer upon completion of the necessary changes, modifications and / or additions, and shall request the Employer to repeat the Guarantee Test until the minimum level of the Guarantees has been met. If the Contractor eventually fails to meet the minimum level of Functional Guarantees, the Employer may consider termination of the Contract, pursuant to GCC Sub-Clause 36.2.2 and the Contractor shall be liable for the amount already paid by the Employer for the Facilities or its part thereof. .............................................. | Referring to the clause of SCC- which states that ' In case of failure to meet the minimum functional guarantee' Contractor shall be liable for the amount already paid by the Employer for the Facilities or its part thereof. We propose as the Contractor is already being penalized through 'Liquidated Damage' on account of shortfall in PG parameters, no further penalty/deduction of any nature shall be applied by PGCIL. | Provision of the Bidding Document shall remain unchanged. | CS to reply
| GCC 22.8 in SCC, Section-V, Vol-I | 22. Defect Liability ..................................... GCC 22.8 If the Facilities or any part thereof cannot be used by reason of such defect and/or making good of such defect, the Defect Liability Period of the Facilities or such part, as the case may be, shall be extended by a period equal to the period during which the Facilities or such part cannot be used by the Employer because of any of the aforesaid reasons. Upon correction of the defects in the Facilities or any part thereof by repair/replacement, such repair/replacement shall have the Defect Liability Period extended by a period mentioned in GCC Sub-Clause 22.2 from the time of such replacement/repair of the facilities or any part thereof. However such extensions shall be limited up to period of 7 years of operation from the date of Taking Over/Completion of Facilities. ..................................... | We propose that such extensions shall be limited up to period of 4 years of operation from the date of Taking Over/Completion of Facilities. Kindly accept | Provision of the Bidding Document shall remain unchanged. | CS to reply
5 | GCC 22.8.1 in SCC, Section-V, Vol-I | GCC 22.8.1 At the end of the Defect Liability Period, the Contractor's Liability ceases except for latent defects. The Contractor's liability for latent defects warranty shall be limited to period of ten (10) years from the end of Defect Liability Period. Latent defects are such defects for which it is established by the Employer that the defect was discovered/noticed after the date of expiration of the Defect Liability Period, but was existing before the expiration of Defect Liability Period and the defects were lying within the material or arising out of design deficiency. Contractor’s liability shall be limited to repair and replacement of defective parts and shall cease upon end of ten years from the date of completion of Defect Liability Period or end of availability & reliability period whichever is later. The provisions contained in the clause will not be applicable: (a) If the Employer has not operated the equipment according to generally approved industrial practices and in accordance with the conditions of operation specified in the Contract by the Contractor and in accordance with operating manuals, if any. (b) In case of normal wear and tear normally applicable to equipment of the type supplied as determined by the Employer. Further, it will not apply to consumables and wearing parts. | We propose that latent defects warranty shall be limited to period of Five(5) years from the end of Defect Liability Period. Kindly accept | Please refer of Amendment No-I. | Please refer Amendment-1 .
6 | ITB 2.1 in BDS, Section-III, Vol-I | ….................................. Further, the firm has to be a ‘Class-I local supplier’ as defined under Public Procurement (Preference to Make in India) Order, 2017 issued by Department for promotion of Industry and Internal Trade (DPIIT), Ministry of Commerce and Industry, Government of India vide order dated 15/06/2017, its revision dated 16/09/2020 (PPP-MII Order) read in conjunction with ‘Public Procurement (Preference to Make in India) to provide for Purchase Preference (linked with local content) in respect of Power Sector’ order dated 16/11/2021 issued by Ministry of Power (MoP Order) and subsequent modifications/ amendments if any Presently, the local content requirement to categorize a supplier as ‘Class-I local supplier’ is minimum 25%. Firms who are not ‘Class-I local supplier‘ shall not be eligible to bid. ......................................... | Since the refurbishment scope is very limited in nature and main equipments like valves & controls shall be supplied from offshore, we request to amend the requirement as "local content requirement exlcuding HVDC system shall be minimum 25%". | Provision of the Bidding Document shall remain unchanged. | Provision of bidding document shall prevail.
| GCC 1.1 (n) & 4.1, Section-IV, Vol-I | 1.1 (n) “Effective Date” means the date of Notification of Award from which the Time for Completion shall be determined 4. Time for Commencement and Completion 4.1 The Contractor shall commence work on the Facilities from the Effective Date of Contract and without prejudice to GCC Sub-Clause 21.2 hereof, the Contractor shall thereafter proceed with the Facilities in accordance with the time schedule specified in the corresponding Appendix – 4 (Time Schedule) to the Contract Agreement. ................................ | We request to modify the definition of "Effective Date" as under: "Effective Date” means the date of Notification of Award from which the Time for Completion shall be determined. Further, time for completion shall be measured from commencement date which is defined as below : "Commencement Date" means the date of fulfilment of all conditions stated below: (a) This Contract Agreement has been duly executed for and on behalf of the Employer and the Contractor. (b) The Employer has paid the Contractor the advance payment within 15 days of receipt of eqvt. advance bank guarantee (ABG) & contract performance bank guarantee (CPBG) from contractor. The Contractor shall submit the ABG & CPBG within 15 days from date of NoA/LoA. Sub Clause 4.1 : The Contractor shall commence work on the Facilities from the Effective Date Commencement Date of Contract and without prejudice to GCC Sub-Clause 21.2 hereof, the Contractor shall thereafter proceed with the Facilities in accordance with the time schedule specified in the corresponding Appendix – 4 (Time Schedule) to the Contract Agreement. | Provision of the Bidding Document shall remain unchanged.
7 | GCC 34.1, Section-IV, Vol-I | 34. Extension of Time for Completion 34.1 The Time(s) for Completion specified in the SCC shall be extended if the Contractor is delayed or impeded in the performance of any of its obligations under the Contract by reason of any of the following: (a) any Change in the Facilities as provided in GCC Clause 33 (b) any occurrence of Force Majeure as provided in GCC Clause 32 (c) any suspension order given by the Employer under GCC Clause 35 hereof or reduction in the rate of progress pursuant to GCC Sub-Clause 35.2 or (d) any changes in laws and regulations as provided in GCC Clause 31 or (e) any other matter specifically mentioned in the Contractby such period as shall be fair and reasonable in all the circumstances and as shall fairly reflect the delay or impediment sustained by the Contractor. | We request to modify the said clause as under : The Time(s) and cost for Completion specified in the SCC shall be extended if the Contractor is delayed or impeded in the performance of any of its obligations under the Contract by reason of any of the following: (a) any Change in the Facilities as provided in GCC Clause 33 (b) any occurrence of Force Majeure as provided in GCC Clause 32 (c) any suspension order given by the Employer under GCC Clause 35 hereof or reduction in the rate of progress pursuant to GCC Sub-Clause 35.2 or suspension by the Contractor under new Clause proposed. (d) any changes in laws and regulations as provided in GCC Clause 31 or (e) any other matter specifically mentioned in the Contract, or (f) any delay or default on the part of the Employer or its other contractors in fulfilling its obligations under the Contract, by such period and amount as shall be fair and reasonable in all the circumstances and as shall fairly reflect the delay or impediment sustained by the Contractor. | Provision of the Bidding Document shall remain unchanged.
8 | GCC 35, Section-IV, Vol-I | GCC 35 Suspension 35.1 The Employer may request the Project Manager, by notice to the Contractor, to order the Contractor to suspend performance of any or all of its obligations under the Contract. Such notice shall specify the obligation of which performance is to be suspended, the effective date of the suspension and the reasons therefor. The Contractor shall thereupon suspend performance of such obligation (except those obligations necessary for the care or preservation of the Facilities) until ordered in writing to resume such performance by the Project Manager. …………….……………………….. | We request to modify the said clause as under : (a) Contract Price properly attributable to the parts of the Facilities executed as on the date of termination including items supplied, products under manufacturing, products ready for inspection or dispatch, products dispatched, services completed or under construction for this contract; (b) any amount paid to subcontractors towards termination of sub-contracts including cancellation charges (c) the costs reasonably incurred by the Contractor in the removal of the Contractor's Equipment from the Site and in the repatriation of the Contractor's and its Subcontractor's personnel (d) costs incurred by the Contractor in protecting the Facilities and leaving the Site in a clean and safe condition (e) the cost of satisfying all other obligations, commitments and claims that the Contractor may in good faith have undertaken with third parties in connection with the Contract and that are not covered by paragraphs (a) through (d) above. | Provision of the Bidding Document shall remain unchanged.
| GCC 36, Section-IV, Vol-I | GCC 36. Termination 36.1 Termination for Employer‟s Convenience 36.1.1 The Employer may at any time terminate the Contract for any reason by giving the Contractor a notice of termination that refers to this GCC Sub-Clause 36.1. ………………… ……………………………….. 36.2 Termination for Contractor‟s Default 36.2.1 The Employer, without prejudice to any other rights or remedies it may possess, may terminate the Contract forthwith in the following circumstances by giving a notice of termination and its reasons therefor to the Contractor, referring to this GCC Sub-Clause 36.2: …………….. …………………………………. | We request to kindly add the following under the provisions of Clause 36: 36A 1: The Contractor may by giving 30 days notice to the Owner, terminate the Contract under the following circumstances: (a) If the Owner: (i) has failed to pay the Contractor the amounts specified in any undisputed invoice, in whole or in part, as may have been invoiced by the Contractor in accordance with the terms and conditions of the Contract or delays in issuing payment security or the Owner (and/or its other contractors ) has defaulted in performaing any of its other obligations in terms of this Contract and the Owner has failed to remedy its default including its payment default within 45 days after the receipt of the Contractor's notice requiring the Owner to remedy such default, or (ii) becomes bankrupt or insolvent... undertaking or assets. 36A 2: In the event of termination of the Contract by the Contractor in terms of Clause 36A 1, the Contractor shall be entitled to payment in accordance with Clause 36.1.3. | Provision of the Bidding Document shall remain unchanged.
9 | GCC 36.1.3, Section-IV, Vol-I | GCC 36. Termination ….............................. 36.1.3 In the event of termination of the Contract under GCC Sub-Clause 36.1.1, the Employer shall pay to the Contractor the following amounts: (a) the Contract Price, properly attributable to the parts of the Facilities executed by the Contractor as of the date of termination (b) the costs reasonably incurred by the Contractor in the removal of the Contractor‟s Equipment from the Site and in the repatriation of the Contractor‟s and its Subcontractors‟ personnel (c) any amounts to be paid by the Contractor to its Subcontractors in connection with the termination of any subcontracts, including any cancellation charges (d) costs incurred by the Contractor in protecting the Facilities and leaving the Site in a clean and safe condition pursuant to paragraph (a) of GCC Sub-Clause 36.1.2 (e) the cost of satisfying all other obligations, commitments and claims that the Contractor may in good faith have undertaken with third parties in connection with the Contract and that are not covered by paragraphs (a) through (d) above. | We request to modify the said clause as under : (a) Contract Price properly attributable to the parts of the Facilities executed as on the date of termination including items supplied, products under manufacturing, products ready for inspection or dispatch, products dispatched, services completed or under construction for this contract; (b) any amount paid to subcontractors towards termination of sub-contracts including cancellation charges (c) the costs reasonably incurred by the Contractor in the removal of the Contractor's Equipment from the Site and in the repatriation of the Contractor's and its Subcontractor's personnel (d) costs incurred by the Contractor in protecting the Facilities and leaving the Site in a clean and safe condition (e) the cost of satisfying all other obligations, commitments and claims that the Contractor may in good faith have undertaken with third parties in connection with the Contract and that are not covered by paragraphs (a) through (d) above. | Provision of the Bidding Document shall remain unchanged.
10 | GCC 32.1, Section-IV, Vol-I | 32. Force Majeure 32.1 “Force Majeure” shall mean any event beyond the reasonable control of the Employer or of the Contractor, as the case may be, and which is unavoidable notwithstanding the reasonable care of the party affected, and shall include, without limitation, the following: (a) war, hostilities or warlike operations (whether war be declared or not), invasion, act of foreign enemy and civil war, (b) rebellion, revolution, insurrection, mutiny, usurpation of government, conspiracy, riot and civil commotion, (c) earthquake, landslide, volcanic activity, flood or cyclone, or other inclement weather condition, nuclear and pressure waves or other natural or physical disaster, | We request to modify the said clause as under : 32.1 “Force Majeure” shall mean any event beyond the reasonable control of the Employer or of the Contractor, as the case may be, and which is unavoidable notwithstanding the reasonable care of the party affected, and shall include, without limitation, the following: (a) war, hostilities or warlike operations (whether war be declared or not), invasion, act of foreign enemy and civil war, (b) rebellion, revolution, insurrection, mutiny, usurpation of government, conspiracy, riot and civil commotion, (c) earthquake, landslide, volcanic activity, flood or cyclone, or other inclement weather condition, nuclear and pressure waves or other natural or physical disaster, (d) Epidemic & Pandemic | Provision of the Bidding Document shall remain unchanged.
| GCC 32.4, Section-IV, Vol-I | 32. Force Majeure ................................... 32.4 The party who has given such notice shall be excused from the performance or punctual performance of its obligations under the Contract for so long as the relevant event of Force Majeure continues and to the extent that such party‟s performance is prevented, hindered or delayed. The Time for Completion shall be extended in accordance with GCC Clause 34. | We request you to please add the following as clause 32.5: If the performance of the Contract is substantially prevented, hindered or delayed owing to Force Majuere for a consecutive period of more than 90 days or an aggregate period of more than 120 days on account of one or more events of Force Majeure during the currency of the Contract the Contractor shall have the right to terminate either the affected portion of the Facilities or the Contract if the event affects the whole Contract. | Provision of the Bidding Document shall remain unchanged.
11 |  |  | We request to modify the said clause as under : The party who has given such notice shall be excused from the performance or punctual performance of its obligations under the Contract for so long as the relevant event of Force Majeure continues and to the extent that such party‟s performance is prevented, hindered or delayed. The Time for Completion shall be extended in accordance with GCC Clause 34. Further, the Contractor will also be entitled to an equitable adjustment of the Contract Price. Further, the Employer recognizes that in case of epidemics or pandemics (or evolution of existing epidemics or pandemics), the precautionary, mitigation or corrective measures implemented by the Contractor in the frame of the Contract are implemented in the best interest of the Employer and the Contract performance, and the Employer and the Contractor both agree that the additional costs reasonably incurred by Contractor in implementing such measures shall be compensated by the Employer to the Contractor. | Provision of the Bidding Document shall remain unchanged.
12 | GCC 33.2.5 Section-IV, Vol-I | 33. Change in the Facilities 33.1 Introducing a Change 33.2.5 The Employer shall issue the Contractor with a Change Order pursuant to GCC Sub-Clause 33.2 by way of amendment to the Contract or in any other manner deemed appropriate. Even if the Employer and the Contractor cannot reach agreement on the price for the Change, an equitable adjustment to the Time for Completion, or any other matters related to the Change Proposal, the Employer may nevertheless instruct the Contractor to proceed with the Change by issue of a “Pending Agreement Change Order” (“Pending Agreement Amendment”). Upon receipt of a Pending Agreement Change Order, the Contractor shall immediately proceed with effecting the Changes covered by such Order. The parties shall thereafter attempt to reach agreement on the outstanding issues under the Change Proposal. If the parties cannot reach agreement within sixty (60) days from the date of issue of the Pending Agreement Change Order, then the matter may be referred to the Arbitrator in accordance with the provisions of GCC Clause 38 & 39. | We request to modify the said clause as under : The Employer shall issue the Contractor with a Change Orderpursuant to GCC Sub-Clause 33.2 by way of amendment to the Contract or in any other manner deemed appropriate. Even if the Employer and the Contractor cannot shall reach agreement on the price for the Change, an equitable adjustment to the Time for Completion, or any other matters related to the Change Proposal, before the the Employer may nevertheless instruct the Contractor to proceeds with the Change by issue of a “Pending Agreement Change Order” (“Pending Agreement Amendment”). Upon receipt of a Pending Agreement Change Order, the Contractor shall immediately proceed with effecting the Changes covered by such Order. The parties shall thereafter attempt to reach agreement on the outstanding issues under the Change Proposal If the parties cannot reach agreement within sixty (60) days from the date of issue of the Pending Agreement Change Order, then the matter may be referred to the Arbitrator in accordance with the provisions of GCC Clause 38 & 39. Futher, the Employer shall not require any Change in case of the following: (i) if the Change shall result in unforeseeable changes in relation to scope (ii) in case goods are not readily available, (iii) in case it has an impact on Guarantees, (iv) in case it has an impact on EHS or an impact on the Contract’s intended purpose. | Provision of the Bidding Document shall remain unchanged.
| Appendix-1 of Contract Agreement, Section-VI,Forms & Proceedures, Vol-I | 2. PAYMENT PROCEDURES 2.1 Method of Payment The Employer shall make payments promptly within thirty (30) days of submission of an invoice/claim by the Contractor, complete in all respects and supported by the requisite documents and fulfillment of stipulated conditions, if any. All the payment shall be released to the Contractor directly. All payments to be made directly to the Contractor shall be made by the Employer though electronic payment mechanism (e-payment) for which necessary details shall be tied up during execution of the Contract. However, a request for payment to be released through cheque shall be considered on case to case basis and merit of the same. | We request to modify the said clause as under : All payments to be made directly to the Contractor shall be made by the Employer though electronic payment mechanism (e-payment) irrevocable letter of credit for which necessary details shall be tied up during execution of the Contract. However, a request for payment to be released through cheque shall be considered on case to case basis and merit of the same. | Provision of the Bidding Document shall remain unchanged.