| S. No | Clause No: | Existing Clause | Amended Clause |
| --- | --- | --- | --- |
|  | Chapter-11 11.9.2 | (b) If the number of occurrences/6 months averaged over the one year period exceeds the guaranteed value, the Contractor shall correct all design deficiencies and equipment defects at no cost to the Employer. | (b) If, at the end of the extended period, the one year average number of occurrences/6 months, disregarding any six consecutive months with the highest number of occurrences/6 months, exceeds the guaranteed value, the Contractor shall correct all design deficiencies and equipment defects at no cost to the Employer |
|  | Chapter-11 11.10.2.1 | …The losses shall be determined for Block 1/2 operation under nominal conditions of ac Busbar voltage (400 KV ), dc voltage (at the rectifier), frequency (50.0 Hz), commutating reactance and firing angles, and with reactive compensation equipment connected from the installed banks and sub banks so as to result in as close to unity power factor operation of the converter station as a whole as possible subject to achieving the harmonic performance levels specified…. | …The losses shall be determined for Block 1/2 operation under nominal conditions of ac Busbar voltage (400 KV ), dc voltage (at the rectifier), frequency (50.0 Hz), commutating reactance and firing angles, and with reactive compensation equipment connected from the installed banks and sub banks so as to result in as close to unity power factor operation of the converter station as a whole as possible subject to achieving the harmonic performance levels specified…. |
|  | Appendix-8(b) (Functional Guarantees), Sample Forms and Procedures, Section-VI | Appendix-8(b) FUNCTIONAL GUARANTEES 1.0 The Facilities and all parts thereof offered shall meet the Functional Guarantees requirements stipulated in Technical Specification. ………………….. …………………………………. Note:* Principal tap is the Tap Position of converter transformer when HVDC converter shall be delivering 1 PU power (250MW per pole) at nominal DC voltage at keeping ac system voltage 400 KV, 50 Hz at 40 degree Celsius ambient temperature. | Appendix-8(b) FUNCTIONAL GUARANTEES 1.0 The Facilities and all parts thereof offered shall meet the Functional Guarantees requirements stipulated in Technical Specification. ………………….. …………………………………. Note:* Principal tap is the Tap Position of converter transformer when HVDC converter shall be delivering 1 PU power (500MW per pole) at nominal DC voltage at keeping ac system voltage 400 KV, 50 Hz at 40 degree Celsius ambient temperature. |
|  | First Envelope and Bid Forms | In view of the above, ‘First_Envelope_and_Bid_Forms_rev01’ excel stand revised as ‘First_Envelope_and_Bid_Forms_rev02’. Note- Bidders are requested to consider the revised excel ‘First_Envelope_and_Bid_Forms_rev02’ for bid preparation/submission. It may be noted that while submitting the bid, Bidders are required to change the excel file name from ‘First_Envelope_and_Bid_Forms_rev02’ to ‘First_Envelope_and_Bid_Forms’. As per the provisions of the portal, it is mandatory to upload the excel file titled ‘First_Envelope_and_Bid_Forms’ (Bidders may refer user manuals at the portal https://etender.powergrid.in regarding submission of bid). |  |