## Clarification No-II
Clarification No-II dated 20.11.2024 to the bidding documents of Refurbishment of HVDC Control, Protection, SCADA, Valve Hall Equipment and Valve Cooling System for 2x500 MW Chandrapur HVDC Back to Back (BTB) Station under Add-Cap; Specification Number: CC/NT/W-HVDC/DOM/A00/24/12849
Sl. No. | Reference Document | Annexure (if applicable) | Clause No. | EXISTING CLAUSE | QUERY DESCRIPTION | POWERGRID REPLY
1. | Chapter-1 |  | 1.2.(a).(xiii) | Space for storage Area is marked in Annexure store Area, approx. 1800 Sqmeter. | .. | Kindly refer sl no 06 provided in Clarification-I.
[5 empty] | 2) Noted. Bidder refers the new drawing provided as per Annexure Store Area rev01 (sr. 11 of Amendment-I). Bidder understands that the site preparatory work for thearea marked within fenced boundary is in scope of the Contractor. .. | Any site preparatory work to complete present scope of work is included in Contractor’s scope.
2. | Chapter-1 |  | 1.3.4.(ii) | Additional Civil work for installation of new equipment like cooler fans foundation, valve cooling system, new store building etc. | a) Noted. Bidder has following follow-up queries:
[5 empty] | (i) Bidder understands that civil works associated with the Closed Store Building will be in accordance with Owner's response to sr. 42 of Clarification-I. | (i) Bidder’s understanding is inline with TS and its issued Clarifications/Amendments
[5 empty] | (ii) Bidder refers the new drawing provided as per Annexure Store Area rev01 (sr. 11 of Amendment-I). Bidder understands that the box area of 90m x 23m indicates the area over which the closed store building is to be built. | (ii)Bidder’s understanding is inline with TS and its issued Clarifications/Amendments
[5 empty] | (iii) A road is shown going through the box area of 90m x 23m. Bidder | (iii) Bidder’s understanding is inline with TS and its issued Clarifications/Amendments
understands that this portion of the road has to be demolished by the Contractor as part of site preparatory work for the new closed store building.
...
3. | Chapter-1 |  | 1.3.4.1 | a) Site preparation including dismantling the existing facilities to accommodate new equipments in the scope of work as per TS. | 2. Noted. Bidder refers the new drawing provided as per Annexure Store Area rev01 wherein a road is shown going through the box area of 90m x 23m. Bidder understands that this portion of the road has to be demolished by the Contractor as part of site preparatory work for the new closed store building. | Bidder’s understanding is inline with TS and its issued Clarifications/Amendments
b) Any Civil works, if required, related to Valve Hall, Valve Cooling System, Valve Cooling UPS, PLC equipment and Cable Trench to be covered in the present scope
of work as per TS.
c) New Store Building in the scope of work as per TS.
4. | Chapter-1 |  | 1.3.4.1.(c) | New Store Building in the scope of work as per TS. | ... | Bidder’s understanding is inline with TS and its issued Clarifications/Amendments
2. Noted. Bidder refers the new drawing provided as per Annexure Store Area rev01 (sr. 11 of Amendment-I) wherein a carpet area of 7m x 6m has been shown in the box area of 90m x 23m. In accordance with Owner's response to sr. no. 21 of Clarification-I, Bidder understands that the rooms in this area shall be airconditioned and appropriate dust ingress protection measures shall be deployed.
...
5. | Chapter-1 |  | 1.3.5.4 | Sensitive equipments shall be stored indoors under controlled environment, if required. | ... | Bidder’s understanding is inline with TS and its issued Clarifications/Amendments
2. Noted. Bidder refers the new drawing provided as per Annexure Store Area rev01 (sr. 11 of Amendment-I) wherein a carpet area of 7m x 6m has been shown in the box area of 90m x 23m. Bidder understands that as a minimum the rooms in this area shall be airconditioned and appropriate dust ingress protection measures shall be deployed.
...
6. | Chapter-8 |  | 8.9.7 | Wall mount fans-20 nos. and Industrial exhaust fans 8 nos. | Noted. Bidder refers the new drawing provided as per Annexure Store Area rev01 (sr. 11 of Amendment-I) wherein a carpet area of 7m x 6m has been shown in the box area of 90m x 23m. Bidder understands that as a minimum the rooms in this area shall be airconditioned and appropriate dust ingress protection measures shall be deployed. | Bidder’s understanding is inline with TS and its issued Clarifications/Amendments
7. | Chapter-8 |  | 8.9.7 | All Civil, Electrical and services works. | ... | Bidder’s understanding is inline with TS and its issued Clarifications/Amendments
- Access road to Store Building and associated areas - Bidder refers the new drawing provided as per Annexure Store Area rev01 wherein a road is shown going through the box area of 90m x 23m. Bidder understands that this portion of the road has to be demolished by the Contractor as part of site preparatory work for the new closed store building.
...
8. | Chapter-8 |  | 8.9.7.6 | For day lighting purpose of GIS hall, minimum 2 mm thick approved translucent polycarbonate sheet shall be provided for wall lighting in addition to windows for at least 10% of wall area on upper portion of both long walls. | Owner is requested to clarify whether Pre-Engineered Store Building as per Cl. 8.9.7 is required or Closed Store Building as per Cl. 8.9.7.6 is required. | Store building shall be of Pre-engineered type as covered under TS Cl 8.9.7
9 | Chapter-11 |  | 11.4.1.4.1 | In a full year the Period Hours are 8760 h (8784 h for a leap year). If the equipment is commissioned part way through a year the period hours shall be proportionately less than 8760 h. (This shall not be | Bidder understands that sr. no. 18 of Amendment-I is being referred. It may be noted that in case the half leap year, full 24 hours will get added due to the leap day (Feb 29). Nevertheles, Owner's definition of 4392 hours is also acceptable. | TS shall prevail
applicable for verification of guarantees).
10 | Chapter-11 |  | 11.10.2.1 | The losses shall be determined for Block 1/2 operation under nominal conditions of ac Busbar voltage (400 KV ), dc voltage (at the rectifier), frequency (50.0 Hz), commutating reactance and firing angles, and with reactive compensation equipment connected from the installed banks and sub banks so as to result in as close to | 1) Bidder refers to the table on page 14 of Chapter 11 under Cl. 11.10.2.1 . Bidder understands that each load level (i.e. 50 MW, 100 MW, 250 MW, 500 MW), the reactive power exchange of the HVDC station shall not exceed the limits specified in TS Cl. 4.3 and 2.4.3. | 1. Bidder’s understanding is inline with TS and its issued Clarifications/Amendments
|  |  |  | unity power factor operation of the converter station as a whole as possible subject to achieving the harmonic performance levels | 2) Owner is requested to clarify the clause no. in TS where the harmonic performance limits for the HVDC station have been specified. | 2.Refer Amendment-II, Sl no 1.
specified.
11 | Chapter-11 |  | 11.10.4 | The Employer undertakes to make an evaluation of no load and Equivalent Load Losses stated by the Bidder in his bid. | Employer is requested to provide information regarding the guaranteed no-load losses (per block) and equivalent load losses (per block) of the station when it was put into commercial operation for the first time. | Please refer TS Cl 11.10 for Losses and Loss Evaluation.
12 | Section-VI: Sample | Appendix 8(b) | Sr. 34 of | FUNCTIONAL GUARANTEES | Bidder understands that 1 PU power corresponds to 500MW per block. Employer is requested to check and issue the necessary amendment. | Refer Amendment-2
| Forms and Procedures (Volume I) |  | Amendment-I | …
|  |  |  | Note: * Principal tap is the Tap Position of converter transformer when HVDC converter shall be delivering 1 PU power (250MW per pole) at nominal DC voltage at keeping ac system voltage 400 KV, 50 Hz at 40 degree Celsius ambient temperature. |  | Note: * Principal tap is the Tap Position of converter transformer when HVDC converter shall be delivering 1 PU power (500MW per pole) at nominal DC voltage at keeping ac system…)
13 | Chapter-11 |  | 11.9.2 | As stated above, the Employer shall monitor the operation of the HVDC system during the guarantee period for each block individually. An annual appraisal of reliability performance shall be jointly made by the Employer and the Contractor to determine whether correction of design deficiencies, if any, is warranted. Evaluation of EOF and transient disturbance shall be made separately. With respect to the guaranteed reliability values for curtailment in HVDC system | Bidder understands that "Transient Disturbance" is no longer one of the | Refer Amendment-2 Sl no 2.
|  |  | (Sr. 30 of | capacity, the following shall apply: | Functional Guarantee parameters. However, the amended text still
|  |  | Amendment-I) | (a) If the number of occurrences/six monthly (EOF/TD) averaged over the 12 months (one year) guarantee period exceeds the | contradicts sr. nos. 19, 22, 27, etc. of Owner's amendment. Hence, Owner is requested to review the clause in entirety and issue the corrections as suggested below:
|  |  |  | guaranteed value, the guarantee period shall be extended by six months. If, at the end of the extended period the one year average number of occurrences/6 months, disregarding any six consecutive months with the highest number of occurrences/6 months, is equal to or lower than the guaranteed number of occurrences/6 months then the reliability guarantee shall be considered as fulfilled | 1. Para-1 may be corrected as follows:
|  |  |  | (b) If the number of occurrences/6 months averaged over the one year period exceeds the guaranteed value, the Contractor shall correct all design deficiencies and equipment defects at no cost to the Employer. | "As stated above, the Employer shall monitor the operation of the HVDC system during the guarantee period for each block individually. An semi- annual appraisal of reliability performance shall be jointly made by the Employer and the Contractor to determine whether correction of design deficiencies, if any, is warranted. Evaluation of EOF shall be made separately. With respect to the guaranteed reliability values for curtailment in HVDC system capacity, the following shall apply:
|  |  |  | ... | 2. Bullet (a) may be corrected in line with sr. no. 27 of Amendment-I.
3. Bullet (b) may be corrected as follows:
"(b) If the number of occurrences/6 months averaged over the one year best two periods of six months each exceeds the guaranteed value, the Contractor shall correct all design deficiencies and equipment defects at no cost to the Employer."
...
14 | Chapter-11 |  | 11.8.1 | ... Also, subject to the terms and conditions specified, the availability per year, considering forced outages, shall be equal to or exceed the guaranteed value. | Bidder requests Employer to correct the discrepancy in the clause as suggested below: | Refer Amendment-1 in this regard
"... Also, subject to the terms and conditions specified, the availability per half-year, considering forced outages, shall be equal to or exceed the guaranteed value."
15 | Chapter-7 |  | 7.4 | In case additional HVAC requirement envisaged by Contractor over and above of existing system, then the additional air condition/ ventilation systems shall be included in the present scope of work to maintain the Valve Hall environmental parameters within the requirement limits of the replaced valve hall. | Bidder understands that the losses on account of additional HVAC system (in case required to maintain the Valve Hall environmental parameters) shall not be considered in the calculation of guaranteed losses as per TS Cl. 11.10. | Bidder’s understanding is in line with TS and its issued Clarifications/Amendments
16 | Chapter-2 |  | 2.2.1 | Valve Hall Temperature: 10 ͘C to 55͘ C | Bidder refers to the maximum & minimum ambient dry bulb one hour average temperature specified under Cl. 2.4.1.1 and maximum ambient relative humidity specified under Cl. 2.4.1.3. | Please refer TS Cl 7.4 for scope of Environment control.
|  |  | 2.4.1.3 | Valve Hall Humidity during operations: <=60 % | Bidder understands that Irrespective of the withstand capacity of the new equipment, the HVDC station may be tripped in case either of the valve hall environmental parameters go beyond the specified limits i.e. temperature below 10 deg C or above 55 deg C or humidity above 60%.