## Clarification No-VI
Clarification No-VI dated 14.01.2025 to the bidding documents of Refurbishment of HVDC Control, Protection, SCADA, Valve Hall Equipment and Valve Cooling System for 2x500 MW Chandrapur HVDC Back to Back (BTB) Station under Add-Cap; Specification Number: CC/NT/W-HVDC/DOM/A00/24/12849
Sr. No. | Volume | Section | Clause No. | Existing Provision | QUERY DESCRIPTION | POWERGRID REPLY as per Clarification No-III dated 20.12.2024 | BIDDER's QUERY | POWERGRID's Reply
1 | Vol II Chapter-1 | SYSTEM ENGINEERING AND STUDIES | 1.3.1.d) | d) All necessary studies to determine the requirements for communication between HVDC station and the remote load despatch centres at at Mumbai (WRLDC) and Bangalore (SRLDC) and RTAMC Nagpur, NTAMC Manesar and Back up NTAMC at Bangalore .. The contractor’s work shall be limited to the design, supply, installation, commissioning and integration of the interface equipment like serial port, modems etc. to communicate with remote load despatch & remote operation centres using IEC 60870-5-101&104 protocol. | The contractor want to understand the total number of connections required from the HVDC gateways for RLDCs, NLDC & NTAMC. Specifically, how many connections will use IEC-104, and how many will use IEC-101 serial? Kindly confirm. | Please refer TS Cl 4.7 and 4.8 regarding this. The channels use IEC-104 to communicate with RLDC and remote control centres. | As per Powergrid's reply vide their Clarification No. III dated 20.12.2024, the contractor understands that the IEC 60870-5-104 protocol is required for communication between the HVDC station and the load despatch centres (SRLDC, WRLDC & NLDC), as well as the remote operation centres (NTAMC, Backup NTAMC & RTAMC). The IEC-101 protocol is not required. Kindly confirm if the Contractor's understanding is correct. | Communication to RLDCs, NLDC, NTAMC, Backup NTAMC & RTAMC shall be on IEC -104 Protocol
2 | Amendment No-I, S.No. 13 | 4 | 4.8.1 | The asynchronous data interface is required for communication between Remote Terminal Units (RTU) to be located at Chandrapur to Southern Regional Load Dispatch Centre (SRLDC), WRLDC (Western region load despatch centre and NLDC (National load despatch centre). | Please confirm the protocol required for data communication to NLDC and the number of connections required from the HVDC gateways to NLDC? | Table in TS Cl 4.8.1 is applicable to communication to WRLDC and SRLDC. Refer TS Cl 4.8 also.
3 | Annexure-NTAMC Remote operation |  | 13 |  | In this architecture, the connection from the HVDC gateways to the RLDC is shown via a router cum firewall. However, in Chapter 4.8.1, communication with WRLDC and SRLDC is requested over IEC-101 serial. The contractor understands that no firewall will be required for IEC-101 serial communication. Additionally, we request that, please share the updated architecture diagram, considering communication with NLDC, WRLDC, SRLDC, NTAMC and NRLDC (if required) from the HVDC gateways. | Present RLDC communication is with IEC-104 protocol. RLDC here means WRLDC, SRLDC.
4 | Volume I | Section VI; Forms & Procedures; Terms and Procedures of Payment | Appendix-1 Clause 1.1 C1 & C2 | Existing provision as per Amendment V is as follows: 1.1 Supply of Goods Portion ………………………. C. Progressive Payment C.1 Twenty percent (20%)^# of the Ex-Works price component of Main Equipment/Materials (excluding Thyristor Valves and all Spares) shall be paid progressively after dispatch of the Equipment/Materials and on submission of documents indicated hereinunder.................... C.2 Twenty percent (20%)## of the Ex-works price of Main Equipment/Materials (excluding Thyristor Valves and all Spares) shall be paid on receipt and storage at site and on physical verification and furnishing of necessary certificate by Employer’s representative......... | We request to kindly accept as below: 1.1 Supply of Goods Portion ………………………. C. Progressive Payment C.1 Twenty Five percent (25%)^# of the Ex-Works price component of Main Equipment/Materials (excluding Thyristor Valves and all Spares) shall be paid progressively after dispatch of the Equipment/Materials and on submission of documents indicated hereinunder.................... C.2 Twenty Five percent (25%)## of the Ex-works price of Main Equipment/Materials (excluding Thyristor Valves and all Spares) shall be paid on receipt and storage at site and on physical verification and furnishing of necessary certificate by Employer’s representative......... |  |  | refer Amendment No-VI
5 | Volume I | Section VI; Forms & Procedures; Terms and Procedures of Payment | Appendix-1 Clause 1.1 D | D. Final Payment Balance 20% (Twenty percent) of the Ex-works price component of Main Equipment/Materials (including Thyristor Valves but excluding all Spares) shall be paid on: a) 05% (Five Percent) on Proof of submission of required number of reproducible, O&M Manuals, approved drawings, data sheets, test report, pamphlets and manuals of mandatory spares, maintenance & testing equipment. b) 15% (Fifteen Percent) on successful completion of erection, testing and commissioning and issuance of Taking Over Certificate. | We request to kindly accept as below: D. Final Payment Balance 10% (Ten percent) of the Ex-works price component of Main Equipment/Materials (including Thyristor Valves but excluding all Spares) shall be paid on: a) 05% (Five Percent) on Proof of submission of required number of reproducible, O&M Manuals, approved drawings, data sheets, test report, pamphlets and manuals of mandatory spares, maintenance & testing equipment. b) 05% (Five Percent) on successful completion of erection, testing and commissioning and issuance of Taking Over Certificate. |  |  | refer Amendment No-VI
6 | Volume I | SCC | S. No. (52) | …...Further, overall capping on the cumulative LD for Availability, Reliability, Station Power Rating, Transient Disturbances and Outage Schedule shall be 15% of Contract Price.... | We request for change as follows: …...Further, overall capping on the cumulative LD for Availability, Reliability, Station Power Rating, Transient Disturbances and Outage Schedule shall be 10% of Contract Price.... |  |  | Provision of the Bidding Document shall remain unchanged.