| Sl. No. | # Volume/ Section | # Clause No. | # Description | # Bidder’s Query | # POWERGRID Reply |
| --- | --- | --- | --- | --- | --- |
| Volume-II (Technical Specifications) |  |  |  |  |  |  |
|  | Volume-II_1- Technical Specification of Tower Test Station | Cl. No. 4.6 Pg. No. 3 of 15 | 4.6 Accreditation Requirement: The contractor shall be responsible for obtaining all necessary accreditations and certifications required for the operation of the Tower Test Station from relevant national or international regulatory bodies (e.g. NABL or equivalent). | Accreditation to ISO 17025 (General Requirements for the Competence of Testing & Calibration Laboratories) is one of the mandatory requirements for testing stations. The standard requires evaluation and approval of the individuals (viz. Quality Manager & Technical Manager) involved in the lab. Need clarification whether the bidder should consider its own manpower or POWERGRID will deploy their employees. This will have impact on costing for O&M. | The bidder shall be responsible for obtaining all necessary accreditations, including ISO 17025. Accordingly, the bidder is expected to deploy its own Quality Manager and Technical Manager for accreditation and operational purposes. While POWERGRID may consider deputing its personnel for training and familiarization with tower test station, the final decision in this regard will be taken during contract execution. However, the overall responsibility for the Operation and Maintenance (O&M) of the Tower Test Station shall rest solely with the vendor. |
|  | Volume-II_1- Technical Specification of Tower Test Station | Cl. No. 4.7 Pg. No. 4 of 15 | 4.7 Drawings: The drawings containing design and engineering details of the Tower Test Station shall be submitted by contractor for approval of POWERGRID before commencing construction activities. This shall be considered within the scope of the contractor, including all associated documentation, audits, and compliance activities. | The timeline for review and approval process at POWERGRID will have impact on overall project delivery period. POWERGRID shall define checkpoints and timeline for approvals. | Timeline for approval and review of the drawing shall be as per POWERGRID standard practice. |
|  | Volume-II_1- Technical Specification of Tower Test Station | Cl. No. 5.1 Pg. No. 5 of 15 | 5.1 Land Identification and Acquisition Purchase and registration of suitable Land on behalf of POWERGRID for establishment of Tower Test Station is envisaged under the scope of the bidder. The land must have a minimum area of 65,000 sq. m, with at least one side having a minimum dimension of 230 meters to accommodate an effective layout and facilitate future expansion The tower test station to be established in Rajasthan near to tower fabricators within 10km radius, such as Jaipur, Dausa. Accordingly, suitable land to be identified. | Firstly, the choice of location is very restricting and will be difficult to meet the requirement such as within 10km radius of tower fabricators. Secondly, as per the current requirement, each bidder is expected to propose three land options. We have concerns about the evaluation process, since the bid price will vary significantly depending on the location and size of the land proposed. Hence, to ensure a level playing field for all bidders, we propose that POWERGRID should take responsibility for acquiring the land. This approach would standardize the basis of bidding and remove location-based cost disparities. | Noted, Land identification and acquisition shall be undertaken by POWERGRID. Refer amendment No -05 |
|  | Volume-II_1- Technical Specification of Tower Test Station | Cl. No. 5.3 Pg. No. 8 of 15 | 5.3 Transverse Mast and Longitudinal Mast Transverse Mast shall be positioned less than 100 meters from the tower test bed. | We reckon the statement should rather read as ‘Transverse Mast shall be positioned not less than 100 meters from the tower test bed’. Need confirmation. | Noted, Refer amendment No -05 |
|  | Volume-II_1- Technical Specification of Tower Test Station | Cl. No. 5.3 Pg. No. 8 of 15 | The beams of the Transverse Mast shall be located at five positions: 15 m, 30 m, 50 m, 70 m and 90 m. These locations are indicative and shall be finalized during detailed engineering. | A load bearing beam (with provision for fixing pulleys) shall be located at 110m as well. Need confirmation. | Noted, Refer amendment No -05 |
|  | Volume-II_1- Technical Specification of Tower Test Station | Cl. No. 5.3 Pg. No. 8 of 15 | The beams of the longitudinal mast shall be located at three positions: 35 m, 55 m, and 85 m. These locations are indicative and shall be finalized during detailed engineering. | A load bearing beam (with provision for fixing pulleys) shall be located at 110m as well. Need confirmation. | Noted, Refer amendment No -05 |
|  | Volume-II_1- Technical Specification of Tower Test Station | Cl. No. 5.13 Pg. No. 11 of 15 | 5.13 Fabrication unit: A suitable size fabrication unit shall be equipped with cutting/shear machine (up to 12mm), drill machine (up to 12mm) & punching machine (12mm) with capability of punching hole 12mm. Suitable size Welding Machine and Hand Grinders shall also be incorporated in the fabrication unit. | The proposed machine capacities of up to 12mm are inadequate. A 765kV tower is expected to use up to 30mm thicknesses, the machine capacities shall be determined accordingly. | The matter shall be discussed and suitably finalized during the first stage bidding discussions. |
|  | Volume-II_1- Technical Specification of Tower Test Station | Cl. No. 5.14 Pg. No. 11 of 15 | 5.14 Office Building: The control room building shall be a G+2 (Ground plus Two Floors) structure with an approximate built-up area of 1200 sqm. The building shall have a provision for a lift with a minimum capacity of 6 persons. The tentative functional allocation of each floor shall be as follows, however the layout shall be finalised at the time of detailed engineering. | The proposed built-up area of 1200 sqm seems to be very high. 330 to 420 sqm should be adequate. Needs confirmation. | The matter shall be discussed and suitably finalized during the first stage bidding discussion. |
|  | Volume-II_1- Technical Specification of Tower Test Station | Cl. No. 5.16 Pg. No. 12 of 15 | 5.16 DG room: Power backup- 250 kVA. Appropriate size DG room shall be constructed. All the necessary equipment, tools and tackles shall be provided. | It is assumed that the scope includes supply of 250kVA DG Set as well. Please confirm. | This is to confirm that the scope includes the supply of a 250 kVA DG set. Refer amendment No -05 |
|  | Volume-II_1- Technical Specification of Tower Test Station | Cl. No. 5.17 Pg. No. 12 of 15 | 5.17 Compressor room: Appropriate size compressor room shall be constructed adjacent to crane. All the necessary equipment, tools and tackles shall be provided. | Compressor specifications are missing. It is assumed that the Bidder can offer suitable compressor along with tools. | The matter shall be discussed and suitably finalized during first-stage bidding discussions. |
|  | General | Tower Test Station Location | The tower test station to be established in Rajasthan near to tower fabricators within 10km radius, such as Jaipur, Dausa. Accordingly, suitable land to be identified. | Furthermore, we would like to submit our observations regarding the location of the proposed Testing Station. Based on our experience, the successful operation of any Testing Station critically depends on the support of a nearby manufacturing facility, backed by a well-maintained supply chain for raw materials and fasteners. In this context, we foresee significant challenges at the proposed location identified by POWERGRID, as there are very limited, if any, manufacturers in the vicinity with the requisite capacity. This could adversely affect timely prototype supply and overall project efficiency. We therefore request POWERGRID to kindly reconsider the proposed location and allow bidders the flexibility to establish the Testing Station closer to their manufacturing plants. This approach will ensure timely availability of prototypes, facilitate effective project control during both construction and O&M phases, and eliminate additional overheads. | Refer amendment No -05 |
|  | Volume-II_1- Technical Specification of Tower Test Station | Cl. No. 9.0 Pg. No. 12 of 15 | 9.0 Bill of Quantity | Sr No; Item; Unit; Quantity; Comments and remarks. 7; Winch (10-ton capacity); Nos; 35; Quantities shall be reconfirmed as it is contradicting in other places.. 10; Load cell; Nos; 100; Load cell capacities shall be mentioned.. 14; Universal Testing Machine (UTM 60 ton); Nos; 1; This UTM is for calibration purpose. An additional UTM (preferably 100ton capacity) will be required for material testing purpose.. | BOQ items shall be discussed and suitably finalized during first-stage bidding discussions. |