| S.No | Document Volume /Section & Page no | Reference Clause | Description in Bidding documents | CLARIFICATIONS RAISED BY BIDDER | POWERGRID’s REPLY |
| --- | --- | --- | --- | --- | --- |
| Volume-II: Technical Specifications |  |  |  |  |  |
| 1 | Vol-II, # Section Project | # Cl. No 2.3 of Technical Specification, Section–Project, Rev.00 | The conditions of roads, capacity of bridges, culverts etc. in the route shall also be assessed by the bidders. The scope of any necessary modification/ extension/ improvement to existing road, bridges, culverts etc. shall be included in the scope of the bidder. The contractor shall carry out the route survey along with the transporter and submit the detail proposal and methodology for transportation of transformer for approval of Purchaser within three months from the date of award. | In view of current situation of Covid in India, we are unable to conduct route survey. # PGCIL is requested to please provide available route survey report to assess the condition of of roads, capacity of bridges, culverts etc | # Bidder to quote meeting the requirement of Technical Specification |
| 2 | Vol-II, # Section Project | Cl. No 3 # Exclusions of Technical Specification, Section–Project, Rev.00 | # Cl. No. 3 (viii) Digital RTCC panel for Bhadla II and Fatehgarh S/S | Pl refer cl. No. 3 (viii) Digital RTCC panel are not required (excluded). But as per BPS schedule 1, we have to consider Digital RTCC relay - 1 no in each site and RTCC panel are not required. # Please confirm our understanding. | # Bidder to quote meeting requirement of clause 3(viii) & 8.3 of Section Project. |
| 3 | Vol-II, Section Project | Cl. No 3 Exclusions of Technical Specification, Section–Project, Rev.00 | Provisions of valves (for future use) for On-line insulating oil drying system, Online, Dissolved Gas (Multi- gas) and Moisture Measuring Equipment, On Line Dissolved Hydrogen and Moisture Monitor and Nitrogen Injection type Fire Prevention & Extinguishing System shall be considered included in the scope. | PGCIL is requested to provide make of the following items: to make provisions in the ICT - Online, Dissolved Gas (Multi-gas) and Moisture Measuring Equipment - On-line insulating oil drying system - On Line Dissolved Hydrogen and Moisture Monitor - Nitrogen Injection type Fire Prevention & Extinguishing System | # Shall be provided to bidder in the event of award. |
| 4 | Vol-II, Section Project | Cl. No 8 Specific requirement of Technical Specification, | Cl. No 8.3 Make and model of Digital RTCC relay ( to be supplied as loose item) shall be decided during detailed Engineering | Pl provide make and model to get vendor offer for our correct estimation. | # Shall be provided to bidder in the event of award. |
| 5 | Vol-II, Section Project | Cl. No 9 of Technical Specification, Section–Project, Rev.00 | 9 Storage of Spare Transformer Unit 9 (iii) The spare Transformer shall be placed on the elevated foundation block to facilitate quick movement. The Transformer unit may be required to be stored for long duration. The spare Transformer unit shall be completely erected. | Since the spare transformer unit shall be completely erected there will not be any long storage of transformers at site. Pl confirm our understanding. Please elaborate the requirement and provide PGCIL detailed procedure for long storage of transformers at site. if we have to consider in our estimation. | # Specification is amply clear. Bidders are to refer to Clause 9 of Section Project. |
| 6 | Vol-I, BPS | 2nd envelope - Price schedule | Requirement of Spares | As per 2nd envelope - Price schedule, we understand that Spares are not required in this tender. | # Mandatory spares for 765kV Transformers are not envisaged under present scope. |
| 7 | Vol-II, Technical Specification- 765kV Transformer Rev 08 | Clause no. 6.1.8 | Tank MS plates of thickness >12 mm should undergo Ultrasonic Test (UT) to check lamination defect, internal impurities in line with ASTM 435 & ASTM 577. | Ultrasonic test shall be done on Raw material at tank supplier end. Kindly accept. | # Noted |
| 8 |  | Clause No. 6.1.10.b | Specific area shall not be provided for jacking pad in the foundation as jacking shall be done by laying temporary metal plates size 400 mm x 400 mm x 32 mm (min) thick. One set of metal plates for jacking of Transformer shall be provided by manufacturer. | Bidder will provide pressure of the jacking point. Design of Metal plate (Size, thk. & Load bearing capacity) shall be decided by foundation/ customer civil engineer. | Supply of metal plates is under present scope, as # per the requirement of bidding document. |
| 9 |  | Clause no. 13.2 | Sufficient number of thermometer pockets fitted with captive screw cap on the inlet and outlet of tank side pipe of cooler bank shall be provided to record temperature during temperature rise test. Suitable arrangement shall be made for bank mounted cooler arrangement. | Thermometer Pocket on 80 NB pipe will restrict the oil flow, Hence, requesting the same shall be provided on common Header & not for all radiators. | # Bidder to quote meeting the requirement of Technical Specification. |
| 10 |  | Clause No. 16 | SCADA Integration and Interconnection | We will provide 4-20mA output for OTI, WTI, however integration and Integration of transformer with existing power system / SCADA system shall not be in bidder's scope. | For OTI & WTI, 4-20mA output is acceptable. # SCADA Integration and Interconnection is not envisaged under present scope. |
| 11 |  | Clause No. 16.1.1 & 16.1.2 | All required power & control cables including optical cable, patch chord (if any) upto Common MB shall be in the scope of contractor. Further, any special cable between CMB to switchyard panel room/control room shall be under the present scope. All cable from RTCC to OLTC Drive Mechanism Box shall be provide (if applicable). Fiber optic cable, power cable, control cables, as applicable, between CMB to switchyard panel room/control room and power supply (AC & DC) to MB and integration of above said IEC-61850 compliant equipment with Substation Automation System shall be under the scope of EPC contractor | All power & control cables from transformer / Reactor accessories to marshalling box shall be in Bidder's scope of supply. Any other control cable / Power cable / FO cable / special cable and accessories shall not be in Bidder's scope. Kindly confirm. | # Bidder to comply the requirement of clause 2.1 (c) of Section Project. |
| 12 |  | Clause No. 18 x | Fibre optic sensor based temperature measuring system (if applicable) | Fiber optic sensor based temperature measuring system is removed from the scope as per section project R01. Hence all relevant clauses are not applicable. | Fiber optic sensor based temperature measuring system is not envisaged under present scope as per Technical Specification. |
| 13 |  | General | Neutral Formation and Earthing Arrangement | Excluded from bidder scope of supply. Kindly confirm. | # Confirmed |
| 14 |  | General | Tertiary Delta Formation | Excluded from bidder scope of supply. Kindly confirm. | # Confirmed |
| 15 |  | General | Short Circuit test | We have neither envisaged carrying Short circuit test on the offered transformer nor any similarity with short circuit tested transformer. | The requirement of Dynamic short circuit (DSC) withstand test for 765kV 500MVA Transformer shall be applicable for the projects for which bid invitation date is after 31st August 2023. Dynamic Short circuit test on 765kV 500MVA Transformer is not envisaged in this package. # For this package, successful bidder has to prove Short-circuit withstand capability including thermal stress for min. 2 Sec during Design review in line with the requirement of IEC 60076-5 and Technical Specification. |
| 17 |  | Cl. No 9 of Technical Specification, Section–Project, Rev.00 | Storage of Spare Transformer Unit | Request you to provide timeline (like for how many months / years) for long storage requirement. | # Spare Transformer shall be utilized as per project/ O&M requirement. Bidder to quote meeting the requirement of clause 9 of Section Project. |
| 18 |  | Cl. No 10 of Technical Specification, Section–Project, Rev.00 | Amendment for change in destination | Request you to provide additional cost like railway crossing removal / fitting and permission to be taken for that which may happen at time of change in destination | # Specification is amply clear. Bidders are to refer to Clause 10 of Section Project.. |
| 19 |  | Earthing of Transformer |  | We understand that connection of transformer to grounding mat is not in the scope of bidder. Please kindly confirm | # Bidder to quote meeting requirement of clause 6.14.4 of Section 765kV Auto Transformer, Rev 8 |
| 20 |  | Digital Relay |  | We understand that only supply of digital relay in the scope of bidder, other works related to Digital relay are excluded from bidder’s scope. Please confirm. | # Bidder to quote meeting requirement of clause 3(viii) & 8.3 of Section Project. |
| 21 |  | Limitation of Space |  | Are there any space constraints for the subjected transformers at site? Please confirm | # Confirmed as no space constraint for the subject transformers at site. |
| 22 |  | Internal Site Access Roads |  | We understand that the Internal Site Access Roads Until the plinth of the transformer are made available by the Owner (or by Owner through relevant authorities) to the Contractor for the Project Works i.e. Movement of Construction Vehicles, Transportation of project Personnel, Equipment etc. Please confirm | # Specification is amply clear. Bidders are to refer to Clause 3(iv) of Section Project, wherein it is mentioned that Civil works for Road within the boundary of all substations is under specific exclusion. |
| 23 |  | Section Project / Clause no. 2.1 .c/ Page No. 3 of 6 |  | We understand that cables between individual MB [IMB] to Common MB [CMB] are excluded from bidder scope. Please Confirm. | # Bidder to quote meeting the requirement of clause 2.1(c) of Section Project. |
| 24 |  | Section Project / Clause no. 2.1 .c/ Page No. 3 of 6 |  | If Cable between individual MB [IMB] to Common MB [CMB] are in bidder’s scope, please provide the cable routing distance between IMB to CMB. | # Shall be provided to the bidder in the event of award. |