## Package I II & III
Clarification No-I (Technical) dated 08/12/2023 to the bidding documents of:
Package-I: Ground Improvement using Vibro Stone Column at KPS-2 Substation associated with Establishment of Khavda Pooling Station-2 (KPS-2) in Khavda RE Park; Spec. No.: CC/T/W-CIVIL/DOM/A00/23/11747, Package-II: Ground Improvement using Vibro Stone Column at KPS-3 Substation associated with Establishment of Khavda Pooling Station-3 (KPS-3) in Khavda RE Park; Spec. No.: CC/T/W-CIVIL/DOM/A00/23/11748, and Package-III: Ground Improvement using Vibro Stone Column for Transmission line corridor between KPS-2 and KPS- 3 associated with Establishment of Khavda Pooling Station-3 (KPS-3) in Khavda RE Park; Spec. No.: CC/T/W-CIVIL/DOM/A00/23/11749.
S. No | Clause as per bidder's query | Package | Clause | Bidder's Queries | Clarification
1 |  |  | Soil Investigation Report | Request you to please provide the Preliminary Soil Investigation report of the Site. | For Package-I and Package-II: Soil Investigation report shall be provided to successful bidder during detailed engineering. For Package-III: Primarily strata consist of ML-CL, SM, CL,SP-SM,MLThe design of stone column is not in contractor’s scope and detail drawings shall be furnished to contractor for execution of work.
2 | Clause 1.2 of Annexure A of Bid Data Sheet | Package 1,2 &3 | Equipment Capabilities | As we understand from the given clause, to bid each package bidder should own or have access to atleast two numbers of machines for installation of Vibro stone columns with bottom feed/ dry feed technique. Please Confirm | The qualification criteria requires bidder to own or have access to min 02 machine to qualify for all packages. However this is not a cumulative requirement.
3 | Clause 1.2 of Annexure A of Bid Data Sheet | Package 1,2 &3 | Technical Experience | Please confirm Technical experience (i) and (ii) are to be in the same contract or Bidder can submit the experience of (i) in one Contract and (ii) in Other Contracts ? | Technial experience (i) and (ii) are not required to be in the same contract.
4 |  |  | Foundation Layout | Please provide us with the following details: 1. Foundation layout (footing width and length) 2.Depth of the footing with respect to FGL and thickness of footing (especially for transmission tower) | Foundation details and layout shall be provided to successful bidder during detailed engineering.
5 |  |  | Location of Transmission Towers | Please provide the exact coordinates of the transmission tower. | For Package-III: Tentative Coordinates of Gantry tower at KPS-2 : Easting - 553106.659 Northing -2663097.219 Gantry tower at KPS-3 : Easting -550793.607 Northing-2677023.45 TL shall emanate from KPS-3 and terminate at KPS-2 in the State of GUJARAT having 40 nos. tower location.
6 |  |  | Technical Details | Please provide the height of the transmission towers, expected overturning moment, allowable settlement and expected loading intensity. | For Package-III: Design of stone column is not in contractor's scope
7 |  |  | Performance Criteria and Safe bearing Capacity | Please provide the Performance criteria for the footings and safe bearing capacities. | The details shall be provided to successful bidder during detailed engineering.
8 |  |  | Level of ground | Please indicate the level of ground at the time of handing over of site. | For Package-I and Package-II: As per clause 1.4 and 1.5 of TS, the bidders are advised to visit the site and fully apprise themselves of the site conditions. Bidder may quote as per BPS and TS. For Package-III: Cutting & Filling is not envisaged in Transmission line Package
9 |  |  | Sequence of vibro stone column installation. | Please confirm the sequence whether the filling to reach FGL will be done first or the vibro stone columns will be installed from EGL and then filling will be done? | For Package-I and Package-II: Installation of stone column shall be done with the existing ground level as on date of installation of stone column. It shall be done upto cut-off level as per approved drawing. For Package-III: Cutting & Filling is not envisaged in Transmission line Package
10 |  |  | Scope of Excavation | We unbderstand that if vibro stone columns are installed from FGL, excavation will be required to lay sand blanket. Please confirm that the scope of excvation is under Bidder's scope or Employer's scope. | For Package-I and Package-II, excavation shall be carried out by respective EPC contractor and co-ordination shall be done by Employer. For Package-III: Please refer Cl. 2C & 17 of Technical Specification
11 | Clause 25.0 Page 57 of GCC | Package 1,2 &3 | The Engineer-in-Charge shall supply dimensioned drawings, levels and other information necessary to enable the Contractor to set out the works and the Contractor shall set out the works and be responsible for the accuracy of the same. | We understand that the design of the ground improvement scheme will be in the scope of Employer(PGCIL) and same shall be carried based on confirmatory soil investigation, geotechnical concerns and structure requirement. It is understood that it is built only job for specialist contractor. Bidder’s scope is limited to installation of vibro stone columns, laying of blanket and conducting post improvement tests. The design is not in Bidder scope and thus only factual data will be furnished of post ground improvement initial field trial tests to have a sanity check on design before start of intallation works. Please confirm. | It is confirmed that the design of ground imrpovement scheme is in the scope of Employer. However, please refer BoQ and TS in regards to scope of work. Conducting pre and post improvement tests as per approved drawing and layout is also in the scope of bidder.
12 | Sl.No 1 of Price Schedule | Package 1,2 &3 | Supply and Installation of 800mm dia vibro stone columns as per approved drawing, using bottom feed method as per IS 15284 (PT-1),2003 as per site requirements including all T&Ps, materials etc. complete in all respect. This includes setting up of column, supplyof required stone aggregate, feeding of the stone from the stone stack, automatic real time monitoring of depth and compactioneffect for each column, preparation of records, submission and preparation of as built drawings etc. The rates are inclusive of allmaterials, labour, T&P etc. required for completion of the work in all respect.Mode of Measurement - For payment purpose, length ofboring shall be measured from Stone Column Cut-off Level to Termination level of Stone Column. | We understand that the Cut off level and EGL Level are same. For avoidance of doubt, please provide the relations of EGL, Working Platform level , FGL and Cut off level. | For Package-I and Package-II: Refer clause 4 (Tentative Design Scheme) of TS in this regard. It is mentioned that approx 2m-4m below FGL shall be the cut-off level depending on the structure and FGL is 7.0M above MSL for Package-I and 5.5M above MSL for Package-II. For further inputs, the bidders are advised to visit the site and fully apprise themselves of the site conditions. For Package-III: Please refer cl. 17 of Technical Specification
13 | Sl. No 4 Page 2 of SFQP | Package 1,2 &3 | Diameter of each stone column to be measured by site engineer as per the approved construction drawing & method statement. | Generally the diameter of stone columns are checked on random based. Checking each column may be practically not possible and time taking procedure for progress. Request you confirm the frequency. | The work shall be carried out as per SFQP.
14 | Sl. No 1 Page No. 6 of SFQP | Package 1,2 &3 | Determination of particle size of Sand of Zone -I or Zone -II | We request you to also consider Zone-III for determination of particle size. The same is considered in the technical specification caluse 8.3. | The work shall be carried out as per SFQP.
15 | Clause 2(C) of Technical Specifications | Package 1,2 &3 | Providing and laying of granular material blanket by using clean medium to coarse sand, over the top of the stone column at cut-off level as per approved drawing. | We understand that the excavation & dewatering is necessary to carry before and parallel to blanketing works. The same will be carried out by PGCIL as there is no item for this activity is mentioned in the Price Schedule and TS. | For Package-I and Package-II: Excavation for laying granular blanket shall be carried out by respective EPC contractor and co-ordination shall be done by Employer. Dewatering, if required, shall be done by bidder for laying granular blanket. The rate is deemed to be included in the blanket work. No extra payment shall be made for dewatering work. For Package-III: Please refer Cl. 2C & 17 of Technical Specification
16 | Cluase 8.3 of Technical Specifications | Package 1,2 &3 | Sand/ fine aggregate of Zone-I, Zone-II and Zone-III as per IS 383 shall be used for sand blanketing. | We understand that Mechanical sand/ crushed sand which has properties inline with Technical specification can be used for blanketing work. | The materials meeting the TS and SFQP requirements can be used for blanketing works.
17 | Sl. No.3 of SCC & GCC 1.0 (dd) | Package 1,2 &3 | Time for Completion | As per tender document the scheduled provided to execute the each package is 04 months, practically the given scheduled will be very difficult to achieve considering the scope & installation & testing. Request you to kindly increase the time period from 04 to 06 months for each package | Bidder shall quote as per provisions of the bidding documents.
18 | Clause No. 6 of Technical Specifications | Package 1,2 &3 | Equipment | The clasue insisting to mobilize o2 Nos of machine in each package. Wherein BDS is asking for own or have access to only 2 machine to qualify for the tender. As we understand if bidder is qualifying for the 3 packages, he needs to own or have access to totally 6 nos of machines. PLease confirm. | The qualification criteria requires bidder to own or have access to min 02 machine to qualify for all packages. However this is not a cumulative requirement. Further, the successful bidder shall have to deploy the machines adequately as per requirement but not less than two numbers for each package.
19 | Clause 2-B of Vol-II Technical Specifications Page 2 of 10 |  | Method of Installing Stone Column | Bidder requests the client to allow the Installation of Stone Columns using the Wet Method. If any technical claridfication required in this regard Bidder will be responsible to take Approval from respected IITs/NITs. | Bidder may quote as per BPS and TS.
20 | Clause 40 of GCC Page 64 of 90 |  | Defect Liability Period | Bidder requests to consider DLP period as 6 months which starts from completion of Ground Improvement Works. | Bidder shall quote as per provisions of the bidding documents.
21 |  |  | Soil Profile | Bidder requests the emplyoyer to share the Soil profile reports for all the three packages. | For Package-I and Package-II: Soil Investigation report shall be provided to successful bidder during detailed engineering. For Package-III: Primarily strata consist of ML-CL, SM, CL,SP-SM,MLThe design of stone column is not in contractor’s scope and detail drawings shall be furnished to contractor for execution of work.
22 | Sr no. 3 09-Section-V-SSC | Page 23 of 30 GCC 1.0 (dd) | Time for Completion: | Considering the time required for mobilization, quantity of Stone column to be executed (especially in package I & II) and granular blanket works including post improvement tests, proposed duration of 4 months is too short. We request you to make it at least 5 to 6 months, for all practical purposes. | Bidder to quote as per provisions of the bidding documents.
23 | Clause 1.1 ANNEXURE-A (BDS) | Page 1 of 2 Technical Experience | The Bidder should have also #successfully completed contracts with total executed quantity of installation of stone column work as per the following: a) One contract not less than 68000 RM for Package-I, 84000 RM for Package-II, 47475.2 RM for Package-III. Or b) Two contracts each not less than 42500 RM for Package-I, 52500 RM for Package-II, 29672 RM for Package-III. Or c) Three contracts each not less than 34000 RM for Package-I, 42000 RM for Package-II, 23737.6 RM for Package-III. | Bidder understands that the stone column works for technical experience can be by Wet Top Feed/ Dry Bottom Feed methods including empty boring and Bidder is allowed to submit same qualification for all packages. In case if bidder wishes to participate in more than one package, the technical requirement remains same and no need to qualify for cumulative requirement. Please confirm. | Confirmed
24 | Clause 1.5 Package-I Technical Specifications for KPS-2 Substation | Page 2 of 10 Site Visit |  | Kindly provide contact person details for site visit | Contact person: Package-I: Sh. Anuj Dubey, Ch. Mgr. Package-II: Sh. Daya Singh, Ch. Mgr. Package-III: Sh. Ghanshyambhai Parsotambhai Bhut, Ch. Mgr. Address: 765/400/220 kV Bhuj Pooling Substation, Village Palanpur (Badi), Taluka- Nakhtrana, Distt. Kutch (Guj.)- 370 001
25 | Clause 5.3 Package-I Technical Specifications for KPS-2 Substation | Page 4 of 10 Sand blanket | A coarse sand pad of around 0.5 m thick covering entire area of stone columns needs to be provided above the cut-off level of stone columns for proper drainage in tower foundations and building area and it should be around 0.3 m thick elsewhere | Considering the scarcity of Sand in the region, we request you to replace the Sand Blanket with Stone Blanket. | Bidder to quote as per BPS and TS.
26 | Clause 7.1 Package-I Technical Specifications for KPS-2 Substation | Page 5 of 10 Setting Out | Contractor should construct and maintain Temporary Benchmarks (TBM) inside the site throughout the construction period as required and as directed by the Engineer in charge. The MSL from the nearby permanent benchmarks should be transferred to the TBM and the levels of the TBM shall be rechecked periodically as directed by the Engineer in charge. | We request transfer of Permanent Benchmark to site shall be arranged by employer. | Permanent benchmark is available at site at one place. All TBM as required for execution of work shall be constructed by bidder and level shall be transferred from permanent benchmark available at site.
27 | Clause 6 Package-I Technical Specifications for KPS-2 Substation | Page 4 of 10 Equipments | In case if stiff / hard layer is encountered within the design treatment depth, predrilling can be used to penetrate till treatment depth. | Since the subsoil information is missing, requirement of Pre-drilling is not clear. Request PCGIL to provide the geotechnical investigation reports of all three packages along with termination criteria for stone columns. | As per clause 1.4 and 1.5 of TS, the bidders are advised to visit the site and fully apprise themselves of the site conditions. Soil Investigation report shall be provided to successful bidder during detailed engineering
28 | Annexure-I SFQP for Vibro Stone Column Works | Page 6 of 7 ACCEPTANCE CRITERIA AND PERMISSIBLE LIMITS FOR STONE AGGREGATE | Sand of Zone-I or Zone-II | As a practice, only stone aggregate is used for Vibro Stone Columns. We request you to exclude Sand (Sand of Zone-I or Zone-II) from gradation of aggregates required for stone column works as mixing sand with aggregate and feeding the same uniformely is practically not feasible. | Bidder to quote as per BPS and TS.
29 | Item no 3 & 4 Price_schedule | Sch-1 Initial Load tests | Waiting Period after Initial Load Tests | We understand that main works can be carried out parallel to the trials works/initial load test without any waiting period. Kindly confirm. | Confirmed
30 | Item no 2 Price_schedule | Sch-1 Granular blanket |  | We understand that Excavation including Backfilling from Ground level to cut off level for testing/ laying of Granular Blanket shall be in other agency scope. Kindly confirm | For Package-I and Package-II: Excavation for laying granular blanket shall be carried out by respective EPC contractor and co-ordination shall be done by Employer. For Package-III. Please refer Cl. 2C & 17 of Technical Specification
31 | Item no 1 Price_schedule | Sch-1 Stone Column installation |  | We understand that contractor is allowed to fill the empty bore (working platform level to cut-off level) with surrounding soil, for safety purpose. | Confirmed. However, measurement of stone column shall be made from cut-off level as per BPS. Nothing shall be paid for empty bore and soil filling in it.
32 | General | Layouts & Drawings | Layouts & Drawings | We request you to provide layout drawings of structures/packages where stone columns has to be executed especially in TL Package the individual tower locations marked. | For Package-I and Package-II: Substation layout drawings shall be provided to successful bidder during detailed engineering. For Package-III: Tentative Coordinates of Gantry tower at KPS-2 : Easting - 553106.659 Northing -2663097.219 Gantry tower at KPS-3 : Easting -550793.607 Northing-2677023.45 TL shall emanate from KPS-3 and terminate at KPS-2 in the State of GUJARAT having 40 nos. tower location.
33 | General | Access roads | Access Roads to work locations | We understand that access roads to work locations, if required, for the machinery/material transportation shall be arranged by client. Kindly confirm | For Package-I and Package-II: Approach road for Substations shall be arranged by Employer. For Package-III: Please refer Cl. 2C & 17 of Technical Specification