## Sheet2
Package - I : Unified Network Management System (U-NMS) for Central Sector and State Sector Communication in NER under Establishment of State of Art Unified Network Management System (U-NMS) for ISTS and State Utility Communication network in North Eastern Region (NER)
S.No | Page Reference | Clause Reference | Clause Description | Query/Request with Justification | PGCIL Response
4 | 6 | Volume II,Part B,Technical Specifications,Section -1 | 1.1.1.4- The UNMS Centre computer system shall be able to collect any data (individually, as scan groups, or collectively) from any of its NMS/EMS/NEs on a non-periodic (demand) basis. Demand scans shall be initiated automatically for an NE whenever the following situations arise: (a) A change of status of NMS/EMS/NEs is detected | Do the NMS support REST API with Event notification capabilities. NMS needs to inform UNMS the event changes happening in order to capture the real time network updates. Also wanted to check of the EMS/NMS support TMF 639 and TMF 638 based APIs | Details of all existing make model has been provided in the TS. Bidder to tie-up with the existing vendors for providing necessary system information.
5 | 8 | Vol 2, Part B, Section 1 | The UNMS system shall prepare all the acquired data for use by the UNMS System applications. The UNMS system shall have capability to accept data from the following sources: (a) Real-time (also referred as telemetered) data received from Existing NMS/National UNMS and NEs | What is the software used for National UNMS and what format is the data be exchanged with National UNMS. | Integration of proposed UNMS with upcoming national UNMS to facilitate data exchange between these UNMSs to facilitate following: a) Visibility of inter-regional links in NER UNMS based on data at national UNMS from other regional UNMSs b) visibility of PAN India network in national UNMS based on data exchanged between national UNMS and regional UNMSs including NER UNMS. c) Updation of PAN India network at national UNMS periodically based on data exchange from regional UNMSs including NER UNMS.
6 | 6 | Volume II PART-A Technical Specification, Section 1.1 | In North Eastern Region, the Regional Load Dispatch Center (NERLDC) is located at Shillong. The other Constituents of North Eastern Region are AEGCL of Assam, MePTCL of Meghalaya, DoP of Arunachal Pradesh , DoP of Nagaland, MSPCLof Manipur, P&E Department of Mizoram TSECL, Tripura.Their existing SLDCs are located at Guwahati, Shillong , Itanagar, Kohima, Imphal, Aizawl, and Agartala respectively | We understand that the proposed U-NMS is to be deployed at 02 locations vis-a-vis Shillong and guwahati, one of it would be MAIN and another as Backup, and rest of the seven location would have to be provided with workstation systems along with required router, firewall, network switches to provide U-NMS conenctivity for their respective states. Kinldy confirm or whether separate U-NMS instances have to be provided at each of these locations. Also the UPs has to be provided only at the 02 locaitons i.e. shillong and guwahati datacenters. Kinldy also confirm that the required conenctivity for these datacenter will be provided by PGCIL. | Confirmed
7 | 7 | Vol. II Part-A Section -1 Point 1.6 | Under this project new UNMS system shall be established at Shillong RTAMC and Guwahati & SLDCs of AEGCL of Assam, MePTCL of eghalaya, DoP of Arunachal Pradesh , DoP of Nagaland, MSPCLof Manipur, P&E Department of Mizoram, TSECL, Tripura of North Eastern Region as per the intent given above.
8 | 8 | Vol. II Part-A Section-1 Point 1.7. e) | Import and Adaption of database & displays made by Employer/Owner for existing NMS system including import of historical data stored in existing servers for integration in new system. | Kindly confirm whether the required schemas and data will be provided by PGCIL to accomplish the historical data migration. | The data shall be fetched from existing NMS as prt of data acquisition.
9 | 9 | Volume II PART-A Technical Specification, Section 1.3 | Multiple proprietary Network Management Systems are provided in North Eastern Region for ISTS/Intra-State Communication management and are deployed for management of specific communication nodes.Some communication nodes are being managed through local craft terminal as the same are not managed by any existing NMSs. | In addition to information provided, we request to kindly share complete information of existing NMS/EMS/Nes like networking equipment, vendor devices, Network Switches/Router, total devices, API/NBI Integration, details of connectivity for Tapping the network to provide conencivity towards proposed U-NMS, to ascertain the deployment and integration efforts. | Bidder to comply TS. If needed, Details in addition to TS may be collected by the Bidder on their own.
10 | 229 | Appendix-A | Existing Upcoming NMS Infrastrucure | Also, NERLDC Shillong mentions equipments from 5 (five) OEM's whereas in B/U NERLDC mentions only from 2 (two) OEM's. Kindly clarify if the information of remaining equipments missed out or is not in place. | There are only two (2) OEMs in B/U NERLDC
11 | 13 | Vol. II Part-A Section-1 Point 1.7. g) | Integration & Testing with new EMS/NMS/NEs coming up during implementation and AMC period of this Contract | Kindly share complete details of the existing as well as Future EMS/NMS/Nes etc. that are planned and will need to be integrated during implementiaton as well as during AMC as these details are required to properly size the solution. Kindly also confirm whether the 20 months delivery period is for integration of existing systems only, and the new NMS/EMS/NEs that come up during implementaton period will be integrated in addition to these 20 months and will not impact the project completion and signoff. | The sizing of the solution shall be done as per Appendix-G.
12 | 19 | Vol. II Part-A Section-1 1.9.2 xviii | Integration of existing equipment and with other planned equipment being procured by Employer/Owner in future. Contractor is responsible for integrating the complete system i.e. upcoming/future network equipment also. |  | Bidder to comply TS. If needed, Details in addition to TS may be collected by the Bidder on their own.
13 | 28 | Vol. II Part-A Section-2 2.2 | Project Schedule Completion schedule of the project is 20 months from the date award of contract agreement .Based upon this the bidder shall submit a preliminary project implementation schedule along with the bid. The detail project implementation schedule shall be submitted by the Contractor after award for Employer’s/Owner’s approval, which shall include at least the following activities: | Kindly share the details of the existing equipment Kindly also confirm whether the 20 months delivery period is for integration of existing systems only, and the new NMS/EMS/NEs that come up during implementaton period will be integrated in addition to these 20 months and will not impact the project completion and signoff. | Bidder to comply TS.
14 | 14 | Vol. II Part-A Section-1 Point 1.7. p) | Additional Hardware, software and services necessary to ensure compatibility with existing equipment
15 | 10 | Volume II PART-A Technical Specification, Section 1.4.1, B | ISTS Communication provided by Private Transmission Agencies | Please share the details of equipments/lines provided by private transmission agencies | Bidder to comply TS. If needed, Details in addition to TS may be collected by the Bidder on their own.
16 | 14 | Vol. II Part-A Section-1 Point 1.7. h) | Integration & Testing with U-NMS at National level coming up during implementation and AMC period of this Contract. | Kindly clarify if there is U-NMS already implemented and in production at NLDC, and that we need to integrate NERLDC UNMS with NLDC. If the above statement is true then please share details of U-NMS at NLDC. | U-NMS at National level shall come in future.
17 | 73 | Vol. II Part-B Section-1 1.2, 1.2.1 | Data Exchange Data Exchange with and National UNMS Centres The UNMS system shall acquire data of inter-regional links & cross-border links by exception calculated, manually entered and transfer time stamped SOE data from NEs & connected UNMS/NMS/EMS over SNMP, CORBA, XML, REST,SOAP,HTML, HTTP or any industry standard protocol. | Our understanding is that the propsoed U-NMS shall facilitate centralized supervision, operation & control of the NE Region and State level Communication system being used for Power System Operation & Monitoring and it will be connected to National U-NMS for central monitoring of the region. However, as per this clause, the proposed U-NMS system shall acquire the data of inter-regional and cross-border links, so does this means that the requirement here is that the proposed U-NMS will act as National U-NMS as well. Kindly confirm and share details as this would considerably impact the U-NMS sizing or ammend the clause accordingly. | The proposed regional U-NMS shall be exchanging data with National U-NMS for inter-regional links & cross border links to get the overall status of the regional communication network.
18 | 73 | Vol. II Part-B Section-1 1.3. (a) | (a) Real-time (also referred as telemetered) data received from Existing NMS/National UNMS and NEs | Kinldy confirm whether the proposed U-NMS will be monitoring the National U-NMS(other regions as well). If not kindly ammend the clause | The proposed regional U-NMS shall be exchanging data with National U-NMS for inter-regional links & cross border links to get the overall status of the regional communication network. This shall not be exchanging data with other regional U-NMSs.
19 | 13 | Volume II PART-A Technical Specification, Section 1.7 (g | Integration & Testing with new EMS/NMS/NEs coming up during implementation and AMC period of this Contract | Request PGCIL to consider the count of NMS/NE's that are implemented and in production at the time of notification of award of contract and when the same is integrated into the new U-NMS the project sign-off to be issued so that new NMS/NE's integration will continue in warranty / AMC. | Bidder to comply TS.
20 | 19 | Vol. II Part-A Section-1 1.9.2 . Xxvi | Tie up with existing communication system provider for providing necessary system information of existing OEMs of Communication system for getting required information for seamless integration with U-NMS system as per requirements mentioned in different sections of Technical Specification. | We understand that the existing equipment like NMS/EMS/NEs etc. are covered under support contract and necessary support for integration will be faclitated by PGCIL. Kindly confirm and also suggest whether the current vendors of NMS/NEs are providing support & maintenance for their equipment. Kinldy confirm what kind of technical tie-up is envisaged, whether its AMC support of existing NMS/NEs or Integration Support with U-NMS or both , so that required commerical aspect can be ascertained | Tie up with existing communication system provider is required for getting necessary system information of existing OEMs of Communication system for seamless integration with U-NMS system. AMC of existing NMS/NEs is not in scope of bidder.
21 | 14 | Vol. II Part-A Section-1 Point 1.7. i) | Technical and Commercial tie-ups with existing vendors for NMS/NEs and OEM’s of U-NMS modules.
22 | 14 | Vol. II Part-A Section-1 Point 1.7. l) | Integration of all the supplied equipments and existing system | We understand that required changes in existing systems and any required NBI Adapters/API for integration will be provided by the existing vendors (except 35 NE which will be directly integrated) and PGCIL will facilitate the same for integration with proposed U-NMS. | Bidder to comply TS.
23 | 14 | Vol. II Part-A Section-1 Point 1.7. m) | The contractor’s scope shall include customization of its database, such as configuration of database, scan period and all other database parameters required to integrate existing system successfully.
24 | 14 | Vol. II Part-A Section-1 Point 1.7. n) | Shifting of existing system workstations and Installation of new system workstations at temporary location in parallel for intervening period. | We understand that the new workstations systems will be deployed at the existing or new locations without any temporary location. Kindly confirm Kindly share details related to shifting involved if any to ascertain the efforts related to cabling etc. | All supplied system shall be installed in existing or new location identified for the system, however, minor civil works may be required to be done by the bidder for installation of the system.
25 | 14 | Vol. II Part-A Section-1 Point 1.7. o) | Shifting and Installation of new system in UNMS Centre. This shall include all the services including cabling, interface modification and shifting or re-shifting of system required for intervening period and for final shifting to main UNMS Centre. Re-cabling for some or all equipments as required for final shifting shall also be in the scope of supplier | We understand that the new U-NMS is to be deployed at 02 lcoations and there is no shifting involved. Kindly confirm and share details related to shifting involved if any to ascertain the efforts related to cabling etc. | Please refer reply at sl. no. 24
26 | 14 | Vol. II Part-A Section-1 Point 1.7. s) | Comprehensive Maintenance of the supplied system for seven (7) years including one (1) year defect liability period as per specification including future UNMS/NMS/EMS & NE Integrations, Database configurations, Maintaining Spare inventory etc. | Kinldy share details of planned Future UNMS/NMS/EMS & NEs that would be integrated to size the solution | The details are provided at Appendix-A.
27 | 16 | Volume II PART-A Technical Specification, Section 1.8.1 | Teaming Agreement of bidder with OEM | Please clarify that the teaming agreement should be submitted at time of acceptance of PO | Yes, the teaming agreement shall be submitted along with the bid.
28 | 18 | Volume II Part A Section-1 1.9.2 | The Contractor shall be responsible for all cabling and wiring associated with the equipment provided both inside and outside buildings. The Contractor shall also be responsible for determining the adequacy of the local power source for the equipment and for cabling to it, with adequate circuit protective breakers, if required. In addition, the Contractor shall be responsible for shielding equipment and cabling to eliminate potential interference to or from the equipment and for earthing of all cabinets and shields as required for system. Contractor's responsibilities include, but are not limited to, the following: | As per our understanding all kinds of civil work shall to be taken care by PGCIL as per clause 1.9.4 (employers responsibility). Kinldy confirm. | Confirmed, however, minor civil works may be required to be done by bidder for installation of the system.
29 | 19 | Volume II Part A Section-1 1.9.2. xiii. | Implement all minor civil works and identify any major civil works i.e. expansion or construction of rooms, trenches necessary for installation of proposed equipment and provide the details of such work to the Employer/Owner.
30 | 19 | Volume II Part A Section-1 1.9.2 . iX. | Buying and maintaining of spares identified under AMC along with main items to meet the contingency during installation and Maintenance period. | Kindly confirm the list of spares to be maintained by the bidder. Please also confirm whether the spares can be maitnained by the bidder at its own warehouse/office locations. | The spare shall be identified and maintained by the bidder to fullfill the requirements of TS.
31 | 33 | Volume II Part A Section-1 2.6.3 2.6.4 2.6.5 2.6.6 | Inspection and Testing | We request that factory inspection and factory tests be waived off for the hardware and software solution and all necessary testing,demo and inspection be done at site during deployment as the project involves complex deployment/integration/configuration based upon the existing NEs/EMS/NMS. Also it will avoid repetetive tasks and provide more time for actual integraton. Kinldy confirm | Bidder to comply TS.
32 | 19 | Volume II Part A Section-1 1.9.2 . Xvi, Xvii | (xvi) Factory and site testing of all hardware and software provided. (xvii) Provide Type Test report to the Employer/Owner and if required, conduct type test. |  | Bidder to comply TS.
33 | 183 | PART- B SECTION-7 INSPECTION AND TESTING 7.1 | 7.1. Inspection, test and availability All materials furnished and all work performed under this Contract shall be inspected and tested. Should any inspections or tests indicate that specific hardware, software, or documentation does not meet the specified requirements; the appropriate items shall be repaired, replaced, upgraded, or added by the Contractor as necessary to correct the noted deficiencies. After correction of deficiencies, all tests necessary to verify the effectiveness of the corrective action taken shall be repeated. Deliverables shall not be shipped until all required inspections and tests have been completed, all deficiencies have been corrected to Employer/Owner's satisfaction and the hardware and software have been approved for shipment by Employer/Owner. 7.2. Inspection Employer/Owner representatives shall be allowed access to the Contractor's facilities during system manufacturing and testing and to any facility where hardware or software is being produced. Office facilities, equipment, and documentation necessary to complete all inspections and to verify that the U-NMS system is being produced and maintained in accordance with the Specification shall be provided to Employer/Owner's representatives by the Contractor. Employer/Owner representatives shall be allowed to review and verify the functional implementation of the U-NMS system software informally in conjunction with scheduled project meetings at the Contractor's facilities. No test plans, procedures or reports are required to support these informal software demonstrations. Employer/Owner representatives shall be allowed to inspect the Contractor's hardware and software quality assurance standards, procedures, and records. The inspection rights described above shall not apply to subcontractors supplying standard computer hardware, peripheral equipment, and third-party software products. The inspection rights shall apply to subcontractors developing new software for inclusion in the U-NMS system and to sub-system suppliers. Generally, equipment items shall be inspected and tested as part of the hardware integration demonstration described in coming sub sections, and third-party software products shall be tested as part of the functional performance test described in coming sub sections. 7.2.1 |  | Bidder to comply TS.
34 | 186-187 | PART- B SECTION-7 INSPECTION AND TESTING 7.8 , 7.8.1 | 7.8. Test Classifications 7.8.1. Factory acceptance Test (FAT): The database, displays and the report formats developed by the contractor for the UNMS system under the scope shall be demonstrated and verified by the Employer/Owner before factory testing. Functions of U-NMS in Main & Backup configuration shall be staged and completely tested with simulated data at the Contractor's facility. The material inspection clearance certificate (MICC) for all hardware shall be issued only after successful completion of FAT as per specification. The data exchange with NMSs/ UNMS national shall be simulated in the factory test environment. Each of the factory tests described below (i.e. the hardware integration test, the functional performance test, and the integrated system test, unstructured tests) shall be carried out under factory test. |  | Bidder to comply TS.
35 | 19 | Volume II Part A Section-1 1.9.2 . Xxv | After successful deployment of UNMS system, all data from Excel sheets and disparate sources shall be migrated to proposed UNMS system so that operations team can work efficiently. | Please share more details on data to be migrated from excel sheets and disparate sources to better assess the migration requirement and delivery plan. | Bidder to Comply TS
36 | 20 | Volume II Part A Section-1 1.9.2. xxxiii | (xxxiii) The Contractor shall ensure following at their own cost, “Any imported quipment/material/item/parts/component to be supplied under the contract shall be tested in the certified laboratories to check for any kind of embedded malware/trojans/cyber threats and for adherence to Indian Standards as per the directions issued by Ministry of Power/Govt. of India from time to time. In case of such import from specified “prior reference” countries, the requirement of prior permission from the Govt. of India including protocol for testing in certified and designated laboratories by Ministry of Power/Govt. Of India”. | All hardware and software will be of reputed make and will be self certified by respective OEM, furthermore, required audit will be done by CERT-in for the solution, so we request waiveoff this assitoonal laboraatory certificate and ammend the clause. | Bidder to Comply TS
37 | 51 | Volume II Part A Section-3 3.4.1 . Vi. | Preventive maintenance activities (Monthly/Quarterly/half yearly/annually) from network operating centers with status reviews and reports. | We request that the Preventive Maintenance be done on Quarterly basis. Kindly consider the request and confirm. | Bidder to Comply TS
38 | 54 | Volume II Part A Section-3 3.4.4.1. iv. | Changes/upgrade/Update in U-NMS application software due to update/upgrade in EMS/NMS application/database software version shall also be provided by contractor without any financial implications to POWERGRID. The EMS/NMS software upgrade/update shall be verified by the U-NMS contractor in lab environment using test server & applications instances as factored in BoQ, in coordination with respective OEM/Vendors within stipulated time approved by the Employer/Owner. The updates/upgrades shall be deployed only after U-NMS contractor has verified the same. The U-NMS contractor shall carry out necessary changes if required due to update/upgrade of underlying EMS/NMS. | Please confirm that the required changes/upgrade/update of existing EMS/NMS will be taken care by their respective OEM/service providers. | Confirmed
39 | 56 | Volume II Part A Section-3 3.4.6 | Spares Management 1. Contractor shall maintain its own inventory of requisite no. of all types of spares required for meeting the U-NMS Application availability requirements as per the specifications. 2. Contractor shall undertake appropriate planning for the storage of spares at strategic locations/ store depots on its own to meet the performance criteria. | Please confirm whether the spare stocking done by OEM of the equipment can be considred or the contracter has to arrange extra spares. Please also share the list of spares to be maintained and whether the contrcater can maitain the spares at its warehouse. | The spare shall be identified and maintained by the bidder to fullfill the requirements of TS.
40 | 59-60 | Volume II Part A Section-3 3.4.9.3 | Less than 99.99% Deduction of 2% of the apportioned price of the apportioned quarterly AMC for every 0.5% or part there of decrease in availability under 99.99%. (Maximum amount of deduction is limited to 100% of AMC charges) | Kindly cap the maximum penalty to 05% of Yearly AMC Charges | Bidder to Comply TS
41 | 72 | Volume II Part B Section-1 1.1.1.5 | Backup Communication Channel Processing Redundant communication channels will be provided between UNMS System (UNMS Centre) and NMS/EMS/NEs . If valid data cannot be acquired from one of the NMS/EMS/NEs, the UNMS System shall automatically failover to the backup Communication channel. A communications failure shall not cause a server failover. The backup communications channel shall be tested periodically up to NMS/EMS/NEs, without manual intervention, to determine its readiness to take over upon failure of the primary channel. An alarm shall be generated for any backup channel that is not ready to take over. A display shall be provided that shows whether each NMS/EMS/NE is being scanned on the primary or backup Communications channel. The user, via this display, shall be able to: (a) Force scanning to a specific channel (primary or backup) (b) Manually fail a channel (c) Inhibit automatic failover of communications (d) Inhibit automatic fail-back of communications. | We understand that the required links for backup channels will be provided by PGCIL for necessary configuration and setup in U-NMS | Confirmed
42 | 140 | Volume II Part B Section-3 3.14, 3.14.14 | Display Types The following list describes the type of displays which are to be included (but not limited to them) in the proposed UNMS system. All Displays shall be having default setting for showing Date & Time. The types of displays are not exhaustive. New types of displays can be added during detail engineering and when required. The display list shall be final after submitted for approval by the contractor. Virtual machine Display If contractor is providing virtualization, the display with following feature should be provided. | We understand that by display type it is meant to be the dashboard/GUI of U-NMS. Kindly confirm. Kinldy also confirm whether all the types of display/GUI has to be provided under U-NMS common display/GUI or separate display/GUI can also be provided for few applications for example Virtualization, Historian etc. as these have their own dedicated displays/GUI provided by OEM and providing these display under U-NMS Display/GUI may not be feasible. | All displays for UNMS applications shall be provided under UNMS common display. For rest services such as virtualization etc., separate displays may be provided .
43 | 147 | Volume II Part B Section-4 4.1.2 | Operating System The operating system of all the equipments of U-NMS system including network equipments shall be latest version. The operating system shall be hardened to provide robust security. In order to facilitate cyber security requirements including patch management, common operating system is preferable to be used by all server nodes within the U-NMS System. | We understand that open-source operating system, virtualization and database can be proposed, kindly confirm. | Bidder to Comply TS
44 | 147 | Volume II Part B Section-4 4.3 | Network Software The network software includes software for network communication, network security and network services. The network software shall be provided for each type of network node connection supplied with the initial system and shall be licensed for the quantities and types of nodes defined for the system configuration. It should be able to generate reports for a defined period regarding availability of communication links. Network Communication: The network communications software shall use a standard network protocol such as TCP/IP. | We understand that by network software its is meant to be U-NMS software and license for nodes to be manged in U-NMS. Kindly clarify. | Confirmed
45 | 168 | Volume II Part B Section-5 5.6 | 5.6 Storage Area Network (SAN) based Storage A SAN (Storage Area Network) based storage shall be provided which shall be sized adequately and shall be used for online storage and all online data backup. Historian shall be connected to the servers through dedicated Fiber optic or Ethernet Port as applicable. The historian system shall facilitate Owner’s Application data storage also. The sizing of the same shall be suitably sized by the contractor to meet the specification requirements. There shall not be any single point failure i.e. there shall be zero down time with single element failure It shall be possible to take and store image backup of all servers & workstations on it. The SAN shall facilitate Employer’s Application Data Storage also | We understand that the a common SAN storage is to be provided for Online data storage, applicaiton data, historian as well as for online data backup adn archiving. Kinldy confirm and also suggest whether by image based backup it is meant to be disk based backup on SAN Storage. Kinldy also confirm the migration data size that has to be migrated to the new U-NMS SAN Storage to provision required capacity | Bidder to propose common or separate storage depending on their configuration meeting the requirements of TS.
46 | 168 | Volume II Part B Section-5 5.6.2 | 5.6.2 Network Area Storage (NAS) A NAS shall be provided for storing image back up of all servers and workstations along with user data. It should be possible to restore or recover any oftware/system at a selected time from back up. | Please confirm whether separate NAS is required as there is requirment of SAN storage asked for application data and image backup mentioned in clause 5.6. If NAS is also to be provided then please share the sizing that has to be planned for SAN and NASrecpectively. | Yes , separate NAS is required and sizing shall be adequate to the meeet the requirements of TS.
47 | 154 | Volume II Part B Section-4 4.8 | Configuration management server Cum Centralized Management Console (CMC) The CMC shall facilitate following activities:  Security / Monitoring to protect systems and network from unauthorised access, manage user access, authorising rights and privileges | We understand that a configuration management server for U-NMS and additonal separate Centralized managment console server for security systems is to be provided. Kinldy confirm | Confirmed
48 | 169 | Volume II Part B Section-5 5.9 | 5.9 Centralized Management Console (CMC) A separate appliance/server/ machine shall be supplied to be used as Centralized Management console for the HIDS, NIPS and firewall & Anti APT (Advance Persistent Threat) Device and Router cum firewall. The management console shall perform the following functions:
49 | 251 | Appendix-B | Project Implementation Schedule | Schedule for Server,SAN,TapeLibrary, Router,Switches, UPS delivery and deployment may also be incorporated. Please also update the supply and installation schedule. | Bidderr shall submit detailed Implementation schedule in the bid
50 | 252 | Appendix-C | BoQ NMS & Element Manager-Software | Please confirm whetger additional NMS and EMS software also need to be provided in addition to U-NMS.Kindly share the details for the use case and requirement for it. | Additional NMS/EMS software may be required for integration of standalone NEs. The requirement shall be identified by the bidder during detailed engineering.
51 | 276 | Appendix-E | The auxiliary memory utilization of any of the server shall not exceed 25% of its delivered capacity. This memory utilization includes the memory used for storage of data for the defined duration as specified in the technical specification | Please confirm whether by auxillary memory it is meant to be Server RAM or SAN Storage or both. | Auxiliary memory refers to Server RAM/ROM.
52 | 253 | Appendix-C | BoQ WAN Router for Server Location | Kinldy confirm quantity of WAN routers and connectivity architecture for U-NMS Routers as there are 06 Routers mentioned whereas its not matchig the Network Architecture provided in Appendix-K for MAIN & Backup control center. Pleas also share the details of existing sites and new sites architecure details as well. | Bidder to Comply TS