## Sheet2
Package - I : Unified Network Management System (U-NMS) for Central Sector and State Sector Communication in NER under Establishment of State of Art Unified Network Management System (U-NMS) for ISTS and State Utility Communication network in North Eastern Region (NER)
Sr No | RFP Reference | Clause Description | Clarification Sought | Reply
1 | Appendix -C BoQ of UNMS, VOL-II Appendix & APPENDIX H AUXILIARY POWER SUPPLY CALCULATION | VRLA TYPE BATTERY BANKS & Criteria for selection of rating of UPS Battery bank: | Kindly confirm details for VRLA in terms of : 1) Battery Backup in hours 2) VAH specific capacity | Bidder to comply TS.
2 | VOL-II PART-C | Each enclosure shall include suitable safety earth networks as per clause 4.2.3.5. Surge protection devices shall be installed in the input ACDB to provide adequate protection against current and voltage transients introduced on input AC due to load switching surges. These protection devices shall be in compliance with IEC- 61312, IEC- 61024 and VDE 0100-534 for following surges: | The mentioned IEC-61313 is obsolete and not supported by any OEMs as on date so please allow the latest version - IEC-61643. | Industry standards meeting our technical specificatios are acceptables.
3 |  | (i) Low Voltage Surges (Class C): Between Requirement R, Y, B & N In≥10kA, 8/20 μS for each phase N & PE In≥20kA, 8/20 μS In = Value of Nominal Discharge Current |  | Industry standards meeting our technical specificatios are acceptables.
4 |  | (ii) Lightning Electromagnetic impulse and other High surges (Class B): Between Requirement R, Y, B & N Iimp≥50kA, 10/350 μS for each phase N & PE Iimp≥100kA, 10/350 μS Iimp = Value of Lightning Impulse Current The blind spots shall be avoided as per IEC 61312-3. |  | Industry standards meeting our technical specificatios are acceptables.
5 | Appendix -C BoQ of UNMS VOL-II Appendix | Video Projection system- Unit (LOT) Qty-1 And 9. Video Projection System (VPS) - Offered by the Contractor | Please share detailed matrix for Video wall e.g. (3 X 2/4 X 2). | Bidder to comply TS.
6 | VOL-II Appendix, Appendix D | 19. Server Panels Sr No -8 : 230V AC, 15/5 A Internal power socket with switch General- Material for rack & Thickness of rack's material | Kindly provide the following details : 1. Bidder need to propose the dual PDU or single PDU in each rack 2. Share details on Material required for rack & Thickness of rack's material. | Bidder to comply TS. If needed, Details in addition to TS may be collected by the Bidder on their own.
7 | VOL-II PART-C, Sec-1 | The connection to the nearest available earthing grid shall be made by the Contractor through 50X6 sq. mm. GI strip with proper protection | As per our understanding, bidder needs to extend earth strip from nearest available earth box/strip for termination of earthing system and preparation of earthing pit is not in Bidder's scope. Kindly confirm if our understanding is correct. | confirmed
8 | VOL-II PART-A, Sec-1 | This specification document states the requirements for the UNMS systems, which the Contractor shall install at Shillong RTAMC and Guwahati & SLDCs of AEGCL of Assam, MePTCL of Meghalaya, DoP of Arunachal Pradesh , DoP of Nagaland, MSPCLof Manipur, P&E Department of Mizoram, TSECL, Tripura of North Eastern Region . Apart from the number of workstations/servers associated with each system, the UNMS configurations shall be identical at main & back-up UNMS centres. | We understood that, bidder needs to prepare supporting infra for UNMS system at all 7 numbers SLDC also. The SOR items mentioned at Shillong & Guwahati will be distributes accordingly. Requesting to Segregate the SOR qty in all 9 locations (SLDC & RTAMCs) and provide additional qty of item list in SOR if required. | Bidder to comply TS.
9 | Vol.II, Appendix-D, S. No 14 - point 13 (WAN Router, page 16) | There shall be 50% spare ports in every router over above the BOQ specified quantity of ports Router should support 1 GB, 10 GB, STM 64 & serial interface. As a minimum 1-G.703 and 10 no. - 1 GB Ethernet ports, 4x10 Gbps Fibre optic ports | Kindly specify the distance and type (Single-Mode / Multi-Mode) of interface 1/10GB. | Single Mode
10 | Vol.II, Appendix-D, S. No 15 - point 7 (LAN Switch, page 17) | 10 Gbps Fibre Optic Ports for Connecting dual Fibre Optic LAN at Server location and State Minimum 8x10 Gbps Fibre Optic Ports and 16x1 Gbps Ethernet ports at Server location Minimum 4x10 Gbps Fibre Optic Ports and 8x1 Gbps Ethernet ports at state | Kindly specify the distance and type (Single-Mode / Multi-Mode) of interface 1/10GB. | Single Mode
11 | Vol. II, Part-B 5.5.2 LAN Switches | Dual LAN is envisaged for the System at Main UNMS Centre and Single LAN for the backup UNMS Centre. | It is understood that, the quantity of L2 switches mentioned in BOQ (Appendix-C) are considered based on the dual LAN at main UNMS and single LAN at back-up UNMS. Please confirm if the understanding is correct. Also please share the scope of extra LAN switches mentioned in SOR for Backup UNMS Centre. | Bidder to comply TS.
12 | Vol. II, Part-B 5.5.2 LAN Switches | Appendix -C BoQ of UNMS WAN ROUTERS for state UNMS NER-Main BOQ (Shillong RTAMC) Qty =14 | As per our understanding, that 14QTY routers has been asked in the Appendix -C BoQ of UNMS for seven SLDCs in HA mode(1+1). Request you please confirm the same whether routers are not required for Main and Backup UNMS Centres of UNMS system in 1+1 mode. If Yes please mention in the BOQ accordingly. Also share quantity distribution of WAN Routers at Main & Backup UNMS Centres. | Bidder to comply TS.
13 | General | Servers and other ICTinfrastructure | Please provide the technical specification of Top of the rack switch along with port type, capacity & density. This helps to stitch the solution. Also please mention the quantity of the switches and also add the respective line item in SOR. | Bidder to comply TS.
14 | Vol. II, Part-B 5.5.2 LAN Switches | Processing capacity Minimum 2 Mpps | Kindly share the switching capacity/ Throughput in Mbps/Gbps in HD/FD mode. | Bidder to comply TS.
15 | Vol. II, Part-B 5.5.2 LAN Switches | 6. Switching capability Layer-3 switching & VLAN | Kindly share the switching capacity/Throughput in Mbps/Gbps in HD/FD mode. | Bidder to comply TS.
16 | Vol. II, Part-B 5.5.2 LAN Switches | All the Routers shall have G.703 Ports as per the system requirement as specified in the relevant appendices of Technical Specification. There shall be 50% spare ports. | Kindly specify the same whether SFP's need to be provided for spare ports or not? | Bidder to comply TS.
17 | Vol. II, Part-B 5.5.2 LAN Switches | e) Turn on logging to a central syslog server. | Please share the specification for syslog server in terms of transactions/logs etc. Please share specification in terms of log retention period. (online & offline storage period) Please mention the same in Appendix -C BoQ of UNMS. | Bidder to comply TS.
18 | Vol. II, Part-B 5.5.2 LAN Switches | Element Manager-Software | Please specify whether EMS to be supplied for Router and Switches. If yes Please mention the same in Appendix -C BoQ of UNMS and add respective line item in SOR. | Bidder to comply TS.
19 |  | The system shall be designed for meeting identified functional and system expansion requirements in all respects including all hardware, software and configurations and the successful bidder shall have to demonstrate the same during Factory Acceptance Test. The operational performance of the system shall meet the Central Electricity Authority (Technical Standards for Communication System in Power System Operations) Regulations, 2020 requirements. | Request you please confirm the detail test cases, Bill of Material & test cases which need to be demonstrated during FAT | Bidder to comply TS.
2.6.6 Field Performance Test
20 | General Requirements | Internet Bandwidth | We understand that any kind of bandwidth (internal, external, Internet & MPLS etc.) will be in scope of Powergrid/CTU. | Confirmed
21 | Vol.II, Part-B, 2.3.3.45 | The system shall provide Network planning & capacity optimization tool to study the following in study/ planning mode of the application: i. Present network scenario for network understanding ii. Planning tool shall have provisions for creating scenarios & creating savecases with version provisioning for State/ Area & Regional networks. iii. Communication Network Capability assessment. iv. Traffic forecasting based on past trends. v. Network planning for fulfilling present services requirements. vi. Exercising different options for network study | The Network planning & capacity optimization tools are specific to the technologies (Eg. SDH, IP/MPLS etc.). Please specify the details of technology to be supported for planning tool. | Bidder to comply TS.
22 |  | Power Grid Corporation of India Ltd. Unified NMS (U-NMS) for ISTS & State Communication network Volume II PART-B Technical Specification for Unified Network Management System (U-NMS) VOL-II PART-B Sec-2 Page 12 of 38
23 |  | vii. Simulation with real time network snapshots for planning and optimization function in Testing and Development environment. viii. For Planning and Optimization activities, the proposed changes have to be implemented in Test & Development environment before deploying in production. ix. Development Model hosted on Development server of the UNMS system shall be exact replica of Real time Communication Topology being used in Production environment. This development server shall also be used for Training Purpose as Training Simulator | Also, as per standard proactive the planning tools are separately deployed and are not part of a UNMS/NMS system, please confirm whether the planning tool can be provided separately of different make/model than UNMS system? | Confirmed meeting the overall PMI requirement
24 | Vol.II, Part-A, 1.7.c | Integration of existing NMS and Network Elements (NE) with Main and Back up UNMS System. One channel of each NMS/NE to Main and Back up UNMS center shall be used for redundancy of respective UNMS Centers. The splitter required for redundant channels integration of NEs shall be in the scope of the contractor. | Please specify the type and quantity of splitters required to protect data channel | Bidder to comply TS. If needed, Details in addition to TS may be collected by the Bidder on their own.
25 | Volume -2 | 3.8 Cyber security System and Monitoring and compliance manager for Critical Infrastructure Protection The Contractor shall also be responsible for monitoring of the cyber security system with cyber security perspective and implementing the monitoring and compliance manager for Critical Infrastructure Protection. The contractor should conduct Cyber Security audit as per Central Electricity Authority (Technical Standards for Communication System in Power System Operations) Regulations, 2020, which state, “ Cyber security. – (1) All users and control/UNMS centres connected to the communication system shall have robust programs in place to adequately and continuously manage cyber security risks that could have adversely impact power system communications infrastructure. (2) The cyber security program shall address the following, namely: - (a) compliance with provisions of the Information Technology Act, 2000 (21 of 2000) and National Cyber Security Policy, 2013 as amended from time to time; (b) implementation of the National Critical Information Infrastructure Protection Centre (NCIIPC) Guidelines; (c) implementation of guidelines and advisories issued by Computer Emergency Response Team (CERT– India) and applicable Sectoral Computer Emergency Response Team (CERT); and (d) compliance to the Central Electricity Authority (Cyber Security) Regulations, as and when they come into force.” | Need more clarity on VAPT scope like number of IPs, frequency of VAPT year are missing. The details technical parameters are also not available i.e.. kind of testing (i). Black/Grey/White and (ii). External/Internal VAPT testing. These details have direct impact on commercials. | It will be as applicable as per relevant standards of cyber security and GOI guidelines being issued time to time
26 | General | General | All UNMS features asked under this RFP scope are dependent on underlying communication system, NE, NMS/EMS, managers', technologies etc. features and capability. Any feature not supported or available are any layers (communication system, NE, NMS/EMS, managers', technologies etc.) shall not be achieved under monitoring & management under UNMS. | Confirmed
27 | General | General | Number of Devices mentioned in - APPENDIX A 'Existing/ Upcoming NE detail of North Eastern Region' is 1800 and - Appendix G - 'SYSTEM SIZING' - Total number of Network Elements (NE) is 2000 - Appendix G - 'SYSTEM SIZING' - Number of NEs to be integrated (not being monitored on any EMS/NMS) - 35 There are difference of about 200 elements. Request to please check and share as required with the respective OEMs & Technological details | Bidder to comply TS. If needed, Details in addition to TS may be collected by the Bidder on their own.
28 | 1.5 Intent of the Project | Integration of existing Network Element (NE) such as Communication Equipment, DCPS etc., existing NMSs and National UNMS with Main & Backup UNMS Centers. | This RFP scope is limited to provision the UNMS at Main & Backup Centres of NERLDC (Shillong & Guwahati) and respective SLDCs and its integration with National UNMS. Please confirm if UNMS is already provisioned at National UNMS Main & Backup Centres (Delhi & Kolkata) | No, National UNMS shall be upcoming in separate package.
29 | 1.5 Intent of the Project | i) Technical and Commercial tie-ups with existing vendors for NMS/NEs and OEM’s of U-NMS modules. | Availability of all the existing OEMs Technical & Commercial tie-up with existing vendors for NMS/NEs should be owned by CTU/POWERGRID. | Bidder to Comply TS
30 | 1.11 Main and Backup UNMS Centre Operational Philosophy | The takeover of main UNMS Center functions by Backup UNMS Center shall require manual intervention. | Request to amend the clause as below: 'The failback of functions to main UNMS Centre functions from Backup UNMS Centre can be manual or automatic' | Bidder to Comply TS
31 | 1.4 Existing Communication System: | B) ISTS Communication provided by Private Transmission Agencies & other IP-MPLS service providers | All the private communication system for Inter or Intra state communications should be monitored & managed by respective service providers. Please confirm if our understanding is correct | Confirmed
32 | 1.15 Applicable Standards | 25. U-NMS/J Standards | Each OSS OEMs has different methods/standards for integrations and suctioning. The standard asked is specific to Java based environment standards. The OSS process and functionality standards are meet with the following standards 'ITIL v3 standard / eTOM standard' So request to remove this clause. | Bidder to Comply TS
33 | 1.3 Data Processing | UNMS system shall have capability to accept data from the following sources: (g) Web Services of Offline Applications | Please share more details and use case for the specific requirement. | Bidder to Comply TS
34 | 1.3.4 Real-time data storage and playback | It shall be possible to playback above stored data on Single Line Diagram and Network Diagram for a configurable time window (configurable from 1 minute to 10 minutes) by defining Start Date, End date, time of window and sampling rate for play back. | The required feature 'playback of stored data on Single Line Diagram and Network Diagram' is not UNMS functionality. Please relax the clause or share the detailed use case for the same. | Bidder to Comply TS
35 | VOL-II PART-B Sec-1 1.6.2.5 Graphical user interface | 1) Drawing tools | The drawing tool is not a functionality of UNMS and can be only fulfilled via separate independent tool. | Bidder to comply TS
36 | BoQ or UNMS | Software & Hardware mentioned line Items in BoQ are : 'NMS & Element Manager-Software' | As per the details in RFP, supply and Provisioning of UNMS and its integration with existing NEs and/or respective NMS is to be done. For NEs with no EMS please share the respective OEMs names and the technology details. Also request to modify the clause/SOR line item as : 'NMS Software', and/or 'NMS Hardware' | Details are provided at Appendix-A. Bidder to comply TS
37 | BoQ or UNMS | TROUBLE TICKETING SYSTEM | Please share the list of ITMS process to be supported like : SLA/Complaint Management, Problem Management, Change Management , Knowledge Management, Release Management, Asset & Spare part Management, Patch management tools. | Bidder to comply TS. If needed, Details in addition to TS may be collected by the Bidder on their own.
38 | PART- B SECTION-1 UNMS FUNCTIONS 1.0 Introduction | b) Network Configuration & Planning - This shall enable user to Design, Assign, Activate/Provision, Configure, Re-Engineer, Network Planning & Capacity Optimization for the Communication system under the scope | This scope is limited to communication systems owned by Powergrid/CTU. And any other communication system owned by 3rd parties will be out of scope of this RFP. Please confirm if our understanding is correct | This scope is for entire ISTS and State Communication Network of NER as per scope of TS
39 | PART- B SECTION-1 UNMS FUNCTIONS 1.0 Introduction | c) Fault Management with Analytics for trending & prediction for the entire communication system | This scope is limited to communication systems owned by Powergrid/CTU. And any other communication system owned by 3rd parties will be out of scope of this RFP. Please confirm if our understanding is correct | This scope is for entire ISTS and State Communication Network of NER as per scope of TS
40 | PART- B SECTION-1 UNMS FUNCTIONS 1.1 UNMS Functions: | Network Element (Any device i.e. Communication Equipment such as SDH,MPLS, PDH, DC Power Supply etc. communicating with UNMS system on SNMP or any Industry standard protocol) Data Acquisition | This scope is limited to communication systems owned by Powergrid/CTU. And any other communication system owned by 3rd parties will be out of scope of this RFP. Please confirm if our understanding is correct | This scope is for entire ISTS and State Communication Network of NER as per scope of TS
41 | PART- B SECTION-1 UNMS FUNCTIONS 1.1 UNMS Functions: | The U-NMS system shall have capability of integration with multiple wired/wireless technologies like SDH, PDH, DWDM, CWDM, ASON, OTN, PTN, MPLS, VSAT, Radio etc. from multiple vendors. | Please amend this clause as : 'The U-NMS system shall have capability of integration with multiple wired/wireless technologies via respective NMS/EMS or direct polling like SDH, PDH, DWDM, CWDM, ASON, OTN, PTN, MPLS, VSAT, Radio etc. from multiple vendors. | Bidder to Comply TS
42 | PART- B SECTION-1 UNMS FUNCTIONS 1.1.1.3 Periodic Scans | Status data shall be reported by exception from the NMS/EMS/NEs and shall be updated and displayed within 4 seconds at UNMS Centre in worst case. A complete scan of all status data from the NMS/EMS/NEs shall be made by exception. | Please amend this clause as : 'Status data shall be reported by exception from the NMS/EMS/NEs and shall be updated and displayed within 2 minutes at UNMS Centre in worst case.' | Bidder to Comply TS
43 | PART- B SECTION-1 UNMS FUNCTIONS 1.1.1.5 Backup Communication Channel Processing | Redundant communication channels will be provided between UNMS System (UNMS Centre) and NMS/EMS/NEs . | We understand that any kind of bandwidth (internal, external, Internet & MPLS etc.) will be in scope of Powergrid/CTU. | Confirmed
44 | PART- B SECTION-1 UNMS FUNCTIONS 1.1.1.5 Backup Communication Channel Processing | The backup communications channel shall be tested periodically up to NMS/EMS/NEs, without manual intervention, to determine its readiness to take over upon failure of the primary channel. | Please define the test intervals and period for the same. | Bidder to Comply TS
45 | PART- B SECTION-1 UNMS FUNCTIONS 1.1.1.5 Backup Communication Channel Processing | The user, via this display, shall be able to: (a) Force scanning to a specific channel (primary or backup) (b) Manually fail a channel. (c) Inhibit automatic failover of communications (d) Inhibit automatic fail-back of communications | Request you to amend the clause as below: The user, via this display or backend or via any means, shall be able to: (a) Force scanning to a specific channel (primary or backup) (b) Manually fail a channel (c) Inhibit automatic failover of communications (d) Inhibit automatic fail-back of communications | Bidder to comply TS
46 | PART- B SECTION-1 UNMS FUNCTIONS 1.3 Data Processing | The UNMS system shall have capability to accept data from the following sources: (a) Real-time (also referred as telemetered) data received from Existing NMS/National UNMS and NEs | Request you to share what all data or any other request types can be pushed from National UNMS Centres like intra-state communication FMS & PMS data, provisioning requests & status etc. | Bidder to comply TS. If needed, Details in addition to TS may be collected by the Bidder on their own.
47 | PART- B SECTION-1 UNMS FUNCTIONS 1.3 Data Processing | Genaral | All kind of data, the reasonability should be confirmed by respective sources in order to process or reject the same. Please confirm if the reasonability will be shared by all respective sources. | Confirmed
48 | PART- B SECTION-1 UNMS FUNCTIONS 1.3 Data Processing | UNMS system shall support processing of same data from minimum Two (2) number of sources for a point i.e. a UNMS point will have multiple sources of data and if one source fails it shall automatically switch to other source (e.g. redundant field data source, Calculation output, Application output etc.) in the order of priority (e.g. priority 1 to redundant field data source, priority 2 to Application output, Priority 3 to Calculation output, etc.) | We understand all the existing data sources are available in redundant mode. Please confirm if our understanding is correct. | Bidder to Comply TS
49 | PART- B SECTION-1 UNMS FUNCTIONS 1.3.2 Calculated Data processing | User shall be able to drag and drop the arguments to define calculation from any display. | Request to amend the clause as below: 'User shall be able to drag and drop or update respective input fields for the arguments to define calculation from any display.' | Bidder to Comply TS
50 | PART- B SECTION-1 UNMS FUNCTIONS 1.3.3 Quality Codes | For calculated data, the presence of a quality code on any of the component data values shall not disrupt the calculation using that value. The quality of the calculated value shall be the quality of its "poorest" component. Results of calculations that are manually overridden by the user shall be denoted with a quality code that can be differentiated from the propagation of a manual entry quality code from one of its component values | Requirement is not clear. Please share more details and respective use cases. | Bidder to comply TS. If needed, Details in addition to TS may be collected by the Bidder on their own.
51 | PART- B SECTION-1 UNMS FUNCTIONS 1.3.4 Real-time data storage and playback | The user shall be able to view the stored data on UNMS system displays such as on Single Line diagram, Network Diagram & Trend display by placing a workstation console monitor in a history mode for a specified time and date. | Request you to please confirm if the historical mode is is referred to the reporting console of UI here. And can be only fulfilled via separate independent tool. | Confirmed
52 | PART- B SECTION-1 UNMS FUNCTIONS 1.3.5 Redundant data Source processing | All data in the UNMS database may be obtained from more than one source and there shall not be any restriction or limit on number of redundant sources for a point. Typically, the “best available” source of the data shall be chosen for use in displays, reports, and other functions. This feature of choosing the best available source is “redundant data source processing” function. The inputs to redundant data processing function shall be called “arguments”, and the chosen source is called the “resultant best value.” The arguments may be NE Data values or the values from proprietary NMS or the values from the backup UNMS centre. The resultant best value shall be stored in the UNMS database with Quality Code. | Requirement is not clear. Please share more details and respective use cases. | Best source of data for a point shall be choosen out of avialble redundant sources. Use cases shall be finalized during detailed engineering.
53 | PART- B SECTION-1 UNMS FUNCTIONS 1.4 Sequence-of-Events (SOE) Recording | The description of each event shall include the device name (Alias Name), in addition to database description name, device state, the date, and the time (to the nearest second) of each event. | Request to please share more details on the database description name here. | Bidder to comply TS. If needed, Details in addition to TS may be collected by the Bidder on their own.
54 | PART- B SECTION-1 UNMS FUNCTIONS 1.5 Remote Configuration | It shall be possible to assign a number of controllable NEs in one group and then control all the devices by executing a single control command on the group | Request you to confirm if by control, it means configuration of NEs and it respective grouping. | A single control command can be for configuration, alarm acknowledgement etc. Bidder to comply TS.
55 | PART- B SECTION-1 UNMS FUNCTIONS 1.6 Information Storage & Retrieval (ISR) System | The ISR System shall capture raw production data in real-time, at its original scan rate from system such as Network resource management, fault management, performance management, trouble ticketing etc. and the same shall be submitted for approval during detail engineering | Request to amend the clause as below: 'The ISR System shall capture raw production data in real-time from NEs, at its original scan rate from system such as Network resource management, fault management, performance management, trouble ticketing etc. and the same shall be submitted for approval during detail engineering. | Bidder to comply TS
56 | PART- B SECTION-1 UNMS FUNCTIONS 1.6 Information Storage & Retrieval (ISR) System | It shall display current and past operating conditions on desktops anywhere and anytime throughout the enterprise and beyond | Request to amend the clause as below: 'It shall display current and past operating conditions on desktops anywhere and anytime throughout the enterprise and beyond' | Bidder to comply TS
57 | PART- B SECTION-1 UNMS FUNCTIONS 1.6.2.3 Calculated values | Calculations shall be started and reset based on time. The ISR System must be able to save calculated values as separate data points. The ISR system shall perform the calculations in real time and allow results to be trended and archived with the raw data without affecting the operations of the source systems. The calculation engine shall be able to define aggregations based on asset type, totalizers (accumulators), and performance equations formulas and shall support periodic or time-based or event-based triggers. The calculations shall be able to be done by asset-based/group-based, instead of per-point bases. All calculations shall provide the re-calculation functionality to automatically or on-demand to re-calculate the historical data. | Request to share details calculation scenarios and mathematical calculations required. | Bidder to comply TS. If needed, Details in addition to TS may be collected by the Bidder on their own.
58 | PART- B SECTION-1 UNMS FUNCTIONS 1.6.2.5 Graphical user interface | 6) Ability for report to carry some manual entry. | Please share more details on this requirement. | Bidder to comply TS
59 | PART- B SECTION-1 UNMS FUNCTIONS 1.6.2.7 Manual data entry | The ISR System shall have the capability to accept manual data also. This information shall be used to complete the picture of operations and required for problem diagnosis or reporting in conjunction with the data collected automatically. Manual data entry shall be allowed from defined clients with audit trail. | Please share all scenarios for Manual data entries to UNMS System including clients/sources. | Bidder to comply TS
60 | PART- B SECTION-1 UNMS FUNCTIONS 1.6.2.7 Manual data entry | The ISR system shall have feature of the manual correction of the archived data with a unique flag. This shall be limited to only to the authorized users. All such changes shall be logged to the audit file for future reference. | 1) Please share the scenarios for manual correction of data in ISR. 2) Also if the data reasonability from any sources is not meet then as defined in PART- B SECTION-1 UNMS FUNCTIONS section 1.3 Data Processing, then also the corrections should be allowed? | 1. Bidder to comply TS. 2. Confirmed
61 | PART- B SECTION-1 UNMS FUNCTIONS 1.6.2.8 Interface with Business Applications | A well-documented API shall be provided to exchange data with third party software. The API must be able to query data and models held within the ISR System. The Historian System must offer connectivity to third party systems using multiple protocols e.g.; OPC/ ODBC/ OLEDB/ JDBC and web services. | 1) Request you to please share the end point applications those will query ISR systems and respective scenarios. 2) The query details with possible filter conditions and ISR data models need to be shared | Bidder to Comply TS
62 | PART- B SECTION-1 UNMS FUNCTIONS 1.6.3 Report Generation (in MS office, pdf, etc. format) | The reports shall also contain the followings – a) Operator entered fields of English & Hindi/other language text, symbols, images, etc. b) Trends and charts (2D and 3D). c) Report embedded with Google map for geographical location performance. | b) Request to amend this clause as 'Trends and Charts (2D and/or 3D). c) The Google map is to be displayed on dashboards and report should be chart 0r tabular format. So request to relax this clause | Bidder to Comply TS
63 | PART- B SECTION-1 UNMS FUNCTIONS 1.6.4 Historical Trending | The Historical trending facility should have feature/facility to 1. Rescale and Re-label axis. 2. 3 dimensional display. 3. Zoom in and Zoom out on data. 4. Selections of points through pointing device preferably drag and drop features. 5. Display the timestamp and value of all the trends for any point on the trend while hovering over it with the mouse. 6. Save the configuration (trend point, sampled interval, trending period etc.) for viewing at later stage. 7. Plot raw, average, interpolated, min and max over a user defined sampled time. | 1) On rescaling and relabelling the axis, the query needs to be changed dynamically. Also users will have facility to build decided queries and attached it to any trending historical report. Hence request to relax this clause 2) The 3D display is required for site or device view and not for historical trends, hence request you to relax this clause. 4) The historical trend will have chats or graphs or related data in tabular format and not device view, hence request to relax this clause | Bidder to Comply TS
64 | PART- B SECTION-1 UNMS FUNCTIONS 1.7.2 Development System Functions | Testing capabilities related to Contractor-supplied system software apply only to the ability to call up employer- generated displays and reports and verify linkages to the database. | Please share more details on the testing capabilities on employer- generated displays and reports and verify linkages to the database. | Bidder to Comply TS
65 | PART- B SECTION-2 UNMS SYSTEM APPLICATIONS FUNCTION 2.1.Introduction This section | The regional server shall have multiple database for each State constituent and Regional/ISTS. | Request to amend the clause as : 'The regional server shall have multiple database or schemas for each State constituent and Regional/ISTS' | Bidder to Comply TS
66 | PART- B SECTION-2 UNMS SYSTEM APPLICATIONS FUNCTION 2.2.Design Requirements for UNMS Applications | UNMS system shall ensure seamless operation & management of Communication network viz. fault Management, Design & Provisioning, Inventory management, Performance monitoring etc. without dependency on underlying NMS/EMS. | To ensure shall ensure seamless operation & management of Communication network, EMS/NMS for respective OEMs is required If not then every existing or new OEMs should allow NE management via standard protocol via any possible reachability. Every OEM will provide the standard protocol and every details required in that case. If OEMs will not have standard protocols then EMS is a must. So request you to relax the clause of no dependency on underlying NMS/EMS. | Bidder to Comply TS
67 | PART- B SECTION-2 UNMS SYSTEM APPLICATIONS FUNCTION 2.2.Design Requirements for UNMS Applications | The system shall have capabilities to take manual inputs for the systems which are not integrated and shall consume & correlate the same for system discovery and O&M. The data processing requirements shall apply to data collected from all specified sources. All input data and parameters, whether collected automatically or entered by a user, shall be checked for reasonability and shall be flagged/ rejected if they are unreasonable. | For network monitoring, maintainace & operations industry standard integration is required. Manual inputs is not a best practice in terms of reasonability, structure, format etc. Request you to dissolve this clause. | Bidder to Comply TS
68 | PART- B SECTION-2 UNMS SYSTEM APPLICATIONS FUNCTION 2.2.Design Requirements for UNMS Applications | All programs and all computer systems shall continue to operate with the old data or manually replaced data in the presence of unreasonable data. | The data reasonability from any sources is not meet then as defined in PART- B SECTION-1 UNMS FUNCTIONS section 1.3 Data Processing it has to be rejected and reported. Hence request to dissolve this clause. | PART-B, SEction 1, Clause 1.3 as reffered by you says "The last valid value of the variable shall be maintained in the database." This is in sync with PART-B, Section 2. So, Bidder to comply TS.
69 | PART- B SECTION-2 UNMS SYSTEM APPLICATIONS FUNCTION 2.2.Design Requirements for UNMS Applications | c) The source codes /web-services based open APIs of the proposed U-NMS application shall be provided to the Employer to allow integration with upper- layer or same layer management systems via WSDL or XML/SOAP/HTTPS etc. | Any solution developed from openSource API can be open source or proprietary solution. So request to relax this clause. | Bidder to Comply TS
70 | PART- B SECTION-2 UNMS SYSTEM APPLICATIONS FUNCTION 2.2.Design Requirements for UNMS Applications | d) Supplied U-NMS system application shall support north bound CORBA/XML/ Q3/SNMP or any other acceptable open standard interface for ensuring integration with other existing/upcoming U-NMS of similar nature. | Request you to amend the clause as below: d) Supplied U-NMS system application shall support north bound CORBA/XML/ Q3/SNMP/HTTP/Rest or any other acceptable open standard interface for ensuring integration with other existing/upcoming U-NMS of similar nature. | Bidder to Comply TS
71 | PART- B SECTION-2 UNMS SYSTEM APPLICATIONS FUNCTION 2.2.Design Requirements for UNMS Applications | e) The supplied UNMS system application shall support data exchange with offline applications such as upcoming or existing ERP system/IT system/Communication system/NMS in standard format like ODBC, OPC, XML, .CSV, .TXT, .XLS etc. ensuring cyber security standards. | Request to share more detail on the offline application data enhance scenarios. | Bidder to Comply TS
72 | PART- B SECTION-2 UNMS SYSTEM APPLICATIONS FUNCTION 2.2.Design Requirements for UNMS Applications | g) The UNMS system application shall have capability for integration and open APIs shall be provided for the integration with Employers other systems such as Billing system, GIS system, ERP system and IT systems. | Request to share more details on other IT systems. | Bidder to comply TS. If needed, Details in addition to TS may be collected by the Bidder on their own.
73 | PART- B SECTION-2 UNMS SYSTEM APPLICATIONS FUNCTION 2.3.Application Functions 2.3.1. Network Resource Management: | It should be possible to define and view a complete Topology of the network in the Network inventory solution. | Please amend the clause as below: 'It should be possible to define and view a complete Topology of the network in the Network inventory Network discovery solution.' | Both Nerwork Inventory and Network Discovery are part of Network Resource Management, so both are applicable.
74 | PART- B SECTION-2 UNMS SYSTEM APPLICATIONS FUNCTION 2.3.Application Functions 2.3.1. Network Resource Management: | The backup communications channel shall be tested periodically up to NE, without manual intervention, to determine its readiness to take over upon failure of the primary channel. | Please amend the clause as below: 'The backup communications channel shall be tested periodically up to NE, with or without manual intervention, to determine its readiness to take over upon failure of the primary channel. | Bidder to Comply TS
75 | PART- B SECTION-2 UNMS SYSTEM APPLICATIONS FUNCTION 2.3.Application Functions 2.3.1. Network Resource Management: | Further, it shall have facility to integrate with more than one of the following applicable sources and discover /capture the inventory from a combination of sources to build the E2E Network inventory: a) Integration with other Existing Inventory Management Systems, if exists. b) Importing from Excel files c) Support in the proposed system for Templates / Rules based inventory building | Request you to please relax the clause c) Support in the proposed system for Templates / Rules based inventory building | Bidder to Comply TS
76 | PART- B SECTION-2 UNMS SYSTEM APPLICATIONS FUNCTION 2.3.2. Communication System Network Model Update: | The communication system model to be used by the application shall reflect present conditions of network as reported by EMS/NMS/NEs, ICCP/ other system data Exchange from connected Control Centres and as entered by the users. | The network and related device status should be only exchanged from EMS/NMS/NEs directly as best practices and no manual ore user inputs should be allowed. Hence please amend the clause as below: 'The communication system model to be used by the application shall reflect present conditions of network as reported by EMS/NMS/NEs, ICCP/ other system data Exchange from connected Control Centres and as entered by the users.' | Bidder to Comply TS
77 | PART- B SECTION-2 UNMS SYSTEM APPLICATIONS FUNCTION 2.3.2. Communication System Network Model Update: | 18) It should provide different reports based on the discovered data and export the data in mutually agreed formats such as .exe /.pdf/.hxml/.doc/.ppt etc. | Request to amend the clause as : 'It should provide different reports based on the discovered data and export the data in mutually agreed formats such as .exe /.pdf/.hxml/.doc/.ppt etc.' | Bidder to Comply TS
78 | PART- B SECTION-2 UNMS SYSTEM APPLICATIONS FUNCTION 2.3.2. Communication System Network Model Update: | 22) The system shall support creation of Virtual Network Elements (VNE) and virtual networks for representing the 3rd party network elements and network respectively. In addition, it must also support addition of inventory to the VNE/Virtual network to provide the end-end view of the circuits passing through 3rd party networks. | The creation and life cycle management of Virtual Network Elements (VNE) and virtual networks are handled by 3rd party applications . | Bidder to Comply TS
79 | PART- B SECTION-2 UNMS SYSTEM APPLICATIONS FUNCTION 2.3.2. Communication System Network Model Update: | 29) The system shall have the capability to add additional parameters or attributes to the discovered data through a GUI to enrich the discovered inventory. | Any manual inputs to inventory of device is not a best practice, this should be only done through recompilation with respective EMS/NSM or through predefined formats. In case it manual parameters are needed then mandatory parameters should not be allowed to be changed manually and shall require user approval at various stages. Hence request to dissolve this clause. | Bidder to Comply TS
80 | PART- B SECTION-2 UNMS SYSTEM APPLICATIONS FUNCTION 2.3.2. Communication System Network Model Update: | 32) The system shall have the capability to expose the discovered data through standard NBI e.g. TMF 814 etc. to external 3rd party systems | Please specify the 3rd party system in this case. | Bidder to comply TS. If needed, Details in addition to TS may be collected by the Bidder on their own.
81 | PART- B SECTION-2 UNMS SYSTEM APPLICATIONS FUNCTION 2.3.2. Communication System Network Model Update: | 33) The system shall have the capability to expand along with the network. The system shall be able to accommodate new vendor, network growth based on network elements, new device types etc. in the proposed system. | Request to amend this clause as below: 'The system shall have the capability to expand along with the network. The system shall be able to accommodate new vendor, network growth based on network elements, new device types etc. in the proposed system. Additional licenses requisition shall be allowed and If at any time system upgrade and additional cost required to accommodate shall required predefined workflow and user approvals ' | Bidder to comply TS. The system shall be sized to accommodate system sizing as per Appendix-G and Expansion requirement.
82 | PART- B SECTION-2 UNMS SYSTEM APPLICATIONS FUNCTION 2.3.2. Communication System Network Model Update: | 35) The system shall have the capability to integrate with Assurance and Fulfilment Systems to provide enriched Inventory. | Request to share more details on Assurance and Fulfilment Systems. | Assurance and Fulfillment system refers to Network Resource Management, Network Configuration & Planning, Fault Management, Performance Management, Troble ticketing, Reporting & Dashboarding.
83 | PART- B SECTION-2 UNMS SYSTEM APPLICATIONS FUNCTION 2.3.2. Communication System Network Model Update: | 38) Discovery and Inventory (Passive): i. The system should be capable of monitoring passive inventory (inventory in stores, issued to contractor for deployment or in transit etc.). | This requirement should be part of Asset management and not of UNMS, hence request to dissolve the clause. | Bidder to Comply TS
84 | PART- B SECTION-2 UNMS SYSTEM APPLICATIONS FUNCTION 2.3.3. Network Configuration and Planning | 9) The proposed system needs to interface with NMS/network elements belonging to different OEMs, supporting different interfaces in the future also. | In future if any new integration protocol needs to be accommodated in proposed UNMS system, then additional licenses will be prequired by Powergrid with required approvals. Request to confirm if the understanding is correct. | Confirmed
85 | PART- B SECTION-2 UNMS SYSTEM APPLICATIONS FUNCTION 2.3.3. Network Configuration and Planning | 13) System shall be able to operate in centralized or de-centralized mode, i.e. the provisioning shall be performed from a central location under Centralized mode requirement and if necessary the provisioning for a particular region / location can also be performed by any user from that particular region / location. | Request to add : with role based user access. | Provision for role based user access is there in the TS. Bidder to comply TS.
86 | PART- B SECTION-2 UNMS SYSTEM APPLICATIONS FUNCTION 2.3.3. Network Configuration and Planning | 14) The system shall support the time component along with any of the dates so that it shall make possible the activation of a service at a particular time and date. | This is scheduled auto Activation process and conflicts with the clause '21) The system shall send provisioning transactions to the NMS/EMS/NE in the real time'. Request to check and update the requirement. | Bidder to Comply TS
87 | PART- B SECTION-2 UNMS SYSTEM APPLICATIONS FUNCTION 2.3.3. Network Configuration and Planning | 17) The offered system shall be configurable & customizable | Any new feature configurable & customizable should be part of Change request. | Confirmed.
88 | PART- B SECTION-2 UNMS SYSTEM APPLICATIONS FUNCTION 2.3.3. Network Configuration and Planning | 23) The system shall support automatic bandwidth grooming feature across multiple Networks. | This is a feature of Orchestrator and not UNMS, hence required to relax this clause . | Bidder to Comply TS
89 | 2.3.3. Network Configuration and Planning | 30) The system shall support concurrent provisioning to various NMS/EMS. | This clause conflict with clause '15) There shall be a front end to monitor the status of the requests and any errors in processing.'. Hence request to check and relax the same. | Bidder to Comply TS
90 | 2.3.3. Network Configuration and Planning | 37) The system shall support creation/deletion/modification of NE level constraints during activation. | Any changes made to the process during an ongoing activation may cause issues and result in failure. Also all the activation parameters should be set as part of planning. Hence required to dissolve this clause. | Bidder to Comply TS
91 | 2.3.3. Network Configuration and Planning | 43) The system shall provide capability to do ring/link optimization by checking free ports in same node/card and suggest possible optimization & take action accordingly. | This is a feature of Orchestrator and not UNMS, hence required to relax this clause . | Bidder to Comply TS
92 | 2.3.4. Fault Management (with Analytics and Trending ) | 7) User privileges and rights should be decided as per requirements of Employer. All activities carried out by any user should be captured in the log. There should be no constraint on no. of users that can be created on FMS window. | No .of users mentioned in specific section will be provisioned into the system initially. For additional user (single/concurrent) requirement respective licences will be procured by CTU/Powergrid if any. Please confirm if the understanding is correct. | No. of Users as per relevant Appendix and expansion criteria shall be provisioned by the bidder.
93 | 2.3.4. Fault Management (with Analytics and Trending ) | 10) Root-cause domain, in which a selected set of current root-cause alarms is displayed in tabular form. Selecting an alarm and invoking an action against it should show the alarms that contributed to the raising of the root-cause alarm. 11) Service-state domain, in which the states of a selected subset of services are displayed. Invoking an action against an alarmed service should show the alarms that contributed to the service being alarmed. 12) Circuit-state domain, in which the current state of selected (generally high-speed) bearers is displayed. Invoking an action against an alarmed circuit should show the alarms that contributed to the circuit being alarmed and the services that are affected. . | Request to share all required correlation categories/scenarios and/or number of the same for system design. | Bidder to comply TS. If needed, Details in addition to TS may be collected by the Bidder on their own.
94 | 2.3.4. Fault Management (with Analytics and Trending ) | 13) The System should provide a high-performance engine to meet the requirement of the integrated alarm system, which can guarantee the normal running of the integrated System especially when the event storm occurs in the network. | Request to add below point to the clause: In such case of event storm, respective filtration/correlation should be done to maintain system performance | Bidder to comply TS
95 | 2.3.4. Fault Management (with Analytics and Trending ) | 14) The System shall provide a comprehensive alarm correlation facility which shall be used for following primary purposes: - a. To determine the root-cause underlying sets of alarms and report the root-cause as a single alarm. b. To assist in reducing the number of alarms seen by engineers to the minimum necessary to effectively manages the network. c. The correlation function shall correlate large number of alarms to identify the underlying problems affecting the network equipment. d. The function shall be used to automate network management tasks. In particular, it shall be used to perform high-level automated actions for Alarm filtering, Alarm aggregation, Alarm enrichment, Root cause analysis and Service impact analysis. | Request to share all required correlation categories/scenarios and/or number of the same for system design. | Bidder to comply TS. If needed, Details in addition to TS may be collected by the Bidder on their own.
96 | 2.3.4. Fault Management (with Analytics and Trending ) | 15) A complete, practical and high-efficient fault association analysis system should be established to meet the network event correlation requirement. Perform automatic association analysis to intra-network or cross-network faults through establishing an association model; assist the network maintenance personnel to correctly analyze and locate the reason for fault events in the shortest period; and establish the association between NE faults and service faults | Request to share all required correlation categories/scenarios and/or number of the same for system design. | Bidder to comply TS. If needed, Details in addition to TS may be collected by the Bidder on their own.
97 | 2.3.4. Fault Management (with Analytics and Trending ) | 20) During network build activities, such as constructing a new trunk route or provisioning a new circuit, alarms may be raised that are irrelevant to the proper functioning of the network. These alarms may be referred to as “build alarms”. The System shall provide facilities that will enable it to identify build alarms and suppress them. | Amend this clause as - build/maintenance alarms | Bidder to Comply TS
98 | 2.3.4. Fault Management (with Analytics and Trending ) | 22) The System shall be able to recognize duplicate alarms by comparing incoming alarms to those already in the current problem list for the reporting object, based on one or more alarm attributes (for example, object name and notification identifier), and automatically suppress such alarms. | Please amend the clause as below: suppress alarm or duplicate the alarm count. | Bidder to Comply TS
99 | 2.3.4. Fault Management (with Analytics and Trending ) | 34) The System shall enable engineer-initiated resynchronization of alarms with selected managed objects, network elements or EMS/NMSs. | Any resynchronization activity is limited to all active alarms in respective EMS & filtration of any kind may result in alarm miss. Hence request to dissolve this clause. | Bidder to Comply TS
100 | 2.3.4. Fault Management (with Analytics and Trending ) | 48) The system shall be able to update the results of SIA while receiving the faults from the network | Request to share more details on SIA in this case. | Bidder to Comply TS
101 | 2.3.8.1.Trouble Ticketing (TT) System: | 1) Effective UNMS Centre operations shall be established based on the IT Infrastructure Library (ITIL) v3 with minimum five analyst to handle incident management and change management. | Request to amend the clause as : Effective UNMS Centre operations shall be established based on the IT Infrastructure Library (ITIL) v3 with minimum five analyst to handle incident management and change management. | Bidder to Comply TS
102 | 2.3.7. Performance Management System (PMS) | 38) Tool shall provide option to integrate with Trouble Ticketing System and Power Level/Current parameter of SFP shall be reported to Ticketing System, before and after restoration of Cable Cut, Partial cut or any failures. | As the resource level performance is be monitored in PMS and respective alarms will be raised in FMS. And based on Alarms correlation and inventories, FMS can detect effected Services and Trouble Ticket should be raised. Request to confirm if our understanding is correct | Confirmed.
103 | 2.3.8.1.Trouble Ticketing (TT) System: | 11) Format of Trouble Tickets (TT) shall be configurable in a flexible way. Several formats of TT should be usable in parallel. | Request to share more details on the format requirement in this case | Bidder to Comply TS
104 | 2.3.8.1.Trouble Ticketing (TT) System: | 12) TT shall be generated in one of the following ways: i. Automatically by Resource Trouble Management based on an alarm in the network ii. Automatically based on predefined schedules for planned maintenance activities iii. Manually by Users of the UNMS Centre and authorized personnel. | Ticket creation should be suppressed for planned maintenance on a particular NE etc. as best practice. Hence request to disole the clause - ii. Automatically based on predefined schedules for planned maintenance activities | Bidder to Comply TS
105 | 2.3.8.1.Trouble Ticketing (TT) System: | 28) The system shall allow modification of ticket on selected parameters. | Request to share details on Ticket modification required in this case | Bidder to Comply TS
106 | 2.4.4. U-NMS Console on Mobile/Handheld | 3) All the functionalities of U-NMS console should be seamlessly available on smart mobile phone with Android, iOS and Windows platform, without any additional software or hardware on server side. | Request to amend the clause as : All the functionalities of U-NMS console should be seamlessly available on smart mobile phone with Android, iOS and Windows platform, without any additional software or hardware on server side. | Bidder to Comply TS
107 | 2.4.5. Dashboards | 1) Dashboard shall be integrated with all applications and shall be extendable to systems such as Trouble Ticketing, Service Provisioning, Service Activation, Inventory System etc. as required. | All the dashboards should be allowed for respective system parts such as Trouble Ticketing, Service Provisioning, Service Activation, Inventory System etc. as required | Bidder to Comply TS
108 | 2.4.6. Reporting | 9) Security violation & cyber threat responds. | All the reports should be allowed for respective system parts such as Trouble Ticketing, Service Provisioning, Service Activation, Inventory System etc. as required | Bidder to Comply TS
109 | 2.5.Generic Integration Requirements: 2.5.1. Integration Points | 2.5.1. Integration Points The Bidder must ensure that UNMS application supports standard internationally acceptable formats, protocols & open standard interface for ensuring the integration with other Employer’s systems such as GIS, ERP & SD-WAN (if required by Employer) at a later date but before the expiry of UNMS contract. | All the integration will be base on industry standard interfaces. Please confirm if the understanding is correct. | Confirmed.
110 | PART- B SECTION-3 USER INTERFACE REQUIREMENTS 3.1 System Users | These users shall be required to login in one or more of following user modes, which include: The Employer/Owner shall be able to assign the operation of certain functions, or features of functions, to specific user modes. It shall be possible to assign user workstations to modes of operation. The functions permitted for each mode shall be defined in a table. Any other type of user shall be decided during detail engineering. | User logins can be categorised based on the Role & groups defined as user authentication & authorization rules based on location & departments. Hence User login with respective modes will ne be required. Request to relax this clause. | Bidder to Comply TS
111 | 3.7 Inventory Detail | Inventory consists of all the equipment, cards, Ports, DCPS, SFPs, Cabinet, Routers, NMS, GPRS, VSAT Servers, Power supply units, etc. installed in the system. Inventory also consists of Spares available with the User of Region/State. | As a best practice, Inventory of spared should be maintained as pert of Asset Management and not in Inventory Management. The spare management should be moved to asset management system. | Bidder to Comply TS
112 | 3.8 Alarms 3.8.4 User Interaction for Alarms | The User shall be able to perform the alarm interactions described below 1) Change Alarm Limits 2) Copy / Paste and export Alarms into an Spreadsheet and all MS-Office formats for offline analysis | 1) Request to share more details on alarm limit change 2) Request to amend the clause as : 'Copy / Paste and export Alarms or direct export into an Spreadsheet and all MS-Office formats for offline analysis' | Alarm limits refer to threshholds at which alarm shall be generated.
113 | 3.8 Alarms 3.8.4.2 Alarm Presentation | 1) Alarm presentation shall be determined by the alarm's category and priority. Displays shall highlight every alarm condition using a combination of colour, intensity, inverse video, and blinking. 2) The alarm condition highlighting shall show whether the alarm has been acknowledged. The highlighted alarm condition shall appear on all displays containing that device or value at all consoles regardless of the alarm's category. | 1) Request to amend clause as: 'Alarm presentation shall be determined by the alarm's category and priority. Displays shall highlight every alarm condition using a combination of colour, intensity, inverse video, and blinking.' 2) This clause contradicts with clause 3.8.2 Alarm Priority levels - (c) Alarm message deleted from alarm summary when acknowledged. Request to please relax this clause. | 1. Bidder to comply TS. 2. Alarm Priority level defines the capability/provisions for the programmer.
114 | 3.14 Display Types 3.14.6 Inventory Display | The display should also provide the inventory of spares present with various Region/users. Various users should be able to enter the spare detail of their concerned region/area manually. The display should provide the Serial Number, Part number, manufacturer, Node where it is installed and any other data required by user. | As a best practice, Inventory of spared should be maintained as pert of Asset Management and not in Inventory Management. The spare management should be moved to Asset management system. | Bidder to Comply TS
115 | PART- B SECTION-5 U-NMS HARDWARE SPECIFICATIONS 5.12 Laptop for Maintenance | The Laptop to facilitate portability. Laptop shall have dual LAN interface and one serial interface. | As per industry standards only single LAN interface are available with all Laptops OEMs. Kindly amend the clause to single LAN Interface or use of any convertors | Use of Converters meeting Technical specification is permissible
129 | RFP Vol 2- Final TS for NER UNMS-Clause 3.4.9.3- Page 12 |  | Since the penalties are supposed to act as deterrents to ensure SLAs during AMC phase, we request that to avoid risk loading by bidders, the penalties during AMC and/or DLP phase are capped at 20% of the quarterly charges. | Bidder to Comply TS
141 | Vol-II(TS) Clause 1.4, Sub clause 1.4.1, Page 10, ISTS Communication: | At present about 2244 kms Fiber Optic Communication Network is in operation and 934 kms under implementation for ISTS. | We understand that required bandwidth and physical link will be provided by PGCIL for integration of existing NE/EMS/NMS with the UNMS. Kindly clarify. | Confirmed
142 | Vol-II(TS) Clause 1.4, Sub clause 1.4.2, Page 10, ISTS Communication: | At present about 1700 kms Fiber Optic Communication Network is in operation and 10482 under implementation for Intra-State Transmission systems of AEGCL of Assam, MePTCL of Meghalaya, DoP of Arunachal Pradesh , DoP of Nagaland, MSPCLof Manipur, P&E Department of Mizoram, TSECL, Tripura
143 | Vol-II(TS) Clause 1.6,Page 12, Overview of the Proposed Systems | The system shall be designed for meeting identified functional and system expansion requirements in all respects including all hardware, software and configurations and the successful bidder shall have to demonstrate the same during Factory Acceptance Test. | In general Factory Acceptance Test (FAT) is a process that evaluates the equipment during and after the assembly process by verifying that it is built and operating in accordance with design specifications. It is mostly for hardware at manufactor's location before shipment. Proof of concept (POC): " functional and system expansion requirements in all respects including all hardware, software and configurations and the successful bidder shall have to demonstrate the same during Factory Acceptance Test." This is identified as POC scope. Please confirm POC needs to be conducted as per the scope detailed. | All functional and system expansion requirement as per TS shall be simulated and tested during FAT
144 | Vol-II(TS) Clause 1.7,Page 13 Scope of Work | d) Development of complete Database, displays and reports either from scratch or by extracting existing database, displays and reports. | It is understood the UNMS application database needs to be populated with existing database records, displays and reports from NMS/EMS. This may needs export/import or data normalization / streamlining. No data is in form of paper records or hardcopy. Please confirm. | Bidder to Comply TS
145 | Vol-II(TS) Clause 1.7,Page 13 Scope of Work | e)Import and Adaption of database & displays made by Employer/Owner for existing NMS system including import of historical data stored in existing servers for integration in new system.
146 | Vol-II(TS) Clause 1.7,Page 13 Scope of Work | g)Integration & Testing with new EMS/NMS/NEs coming up during implementation and AMC period of this Contract. | It is assumed all future NEs will be integrated EMS/NMS (no standalone NEs) as part of PGCIL's furture newtork expansion requirement (not in the scope of this RFP). All such NMS/EMS will require to be integrated with UNMS.It is understood that the SI will only be responsible for providing the integration support at UNMS end over standard APIs without additonal commercials. | There may be upcoming standalone NEs and same need to be integrated with the proposed UNMS during implementation and AMC period of this Contract. Bidder to comply TS.
147 | Vol-II(TS) Clause 1.7,Page 13 Scope of Work | g)Integration & Testing with new EMS/NMS/NEs coming up during implementation and AMC period of this Contract. | Understand that all the existing network elements are in operation of PGCIL and any changes / configuration in terms of visit to site will be carried out by PGCIL personnel. Kindly confirm. | Bidder to Comply TS
148 | Vol-II(TS) Clause 1.7,Page 14 Scope of Work | i) Technical and Commercial tie-ups with existing vendors for NMS/NEs and OEM’s of UNMS modules. | All the details of the existing NMS/EMS/NE's vendors to be provided by PGCIL for future tie-ups | Details are provided at Appendix-A. Bidder to comply TS.
149 | Vol-II(TS) Clause 1.7,Page 14 Scope of Work | j)Supply of Spares identified under AMC along with main items to meet the contingency during installation period and during AMC period | We understand that the spares for the proposed network is only in the scope of SI. Spares for the existing Network elements/EMS will be the responsibility of PGCIL. Kindly confirm | Confirmed
150 | Vol-II(TS) Clause 1.7,Page 14 Scope of Work | i)Integration of all the supplied equipments and existing system | 1) Any protocol limitation or Proprietary solution deployment will restrict integration of NEs with UNMS. 2) Incase incumbent vendor not willing to provide integration support or additonal hardware (new NMS) to enable integration with existing NEs, the same shall be raised to customer to support. Customer to enable joint discussion with incumbent vendors towards closure. 3) Any delay due to unavailaibility/support from the existing vendor/OEM to be excluded from SI's scope. Details of the interfaces/API's to be provided by PGCIL | Bidder to Comply TS
267 | Vol I, Annexure A-BDS Clause No 2.2(B), Page 2 | The bidder must have an association with a firm who has its own UNMS/OSS product which have been installed & commissioned in at least two (2) UNMS/OSS project in the last seven (7) years meeting the requirement mentioned at 2.1(B) above and of which at least one project is in successful* operation for at least one (1) year as on date of bid opening mentioned above. The Bidder shall furnish a joint deed of undertaking executed by him and his associate for the successful performance of the entire system as per the format specified in Section – VI: Sample Forms and Procedures, of the Bidding Documents along with additional Contract Performance Guarantee equivalent to 10% of the Ex-works cost of UNMS from the associate firm whose product is being offered. | We understand this technical experience criteria is applicable for UNMS/OSS Product OEM. The proposed product might be executed by OEM itself or by any other system integrators in other two projects to different customers in last 7 years. As we are Bidding as a System Integrator in this PGCIL opportunity, we can use those project credentials where our associate is UNMS/OSS product OEM. Please confirm if our understanding is correct. | QR related queries initiated via separate note.
268 | Vol I, Annexure A-BDS Clause No 2.2(B), Page 2 | The bidder must have an association with a firm who has its own UNMS/OSS product which have been installed & commissioned in at least two (2) UNMS/OSS project in the last seven (7) years meeting the requirement mentioned at 2.1(B) above and of which at least one project is in successful* operation for at least one (1) year as on date of bid opening mentioned above. The Bidder shall furnish a joint deed of undertaking executed by him and his associate for the successful performance of the entire system as per the format specified in Section – VI: Sample Forms and Procedures, of the Bidding Documents along with additional Contract Performance Guarantee equivalent to 10% of the Ex-works cost of UNMS from the associate firm whose product is being offered. | Please confirm if UNMS/OSS Product OEM can sign joint deed of undertaking to be associate will multiple Bidders and submit the same technical experience certificates as part of their bids. | QR related queries initiated via separate note.
269 | Vol I, Annexure A-BDS Clause No 2.1(B), Page 1 | UNMS Product in each of the above projects must have following: | We undertsand the clause is: UNMS/OSS Product in each of the above projects must have following: | QR related queries initiated via separate note.