| Clarification-I for Replacement of old static & Electromechanical Relays of ICT/Reactors with latest numerical relays at various stations of NR-III; (Specification No.: 5002001112/OTHERS/DOM/K00 - NR3 RHQ -1) |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Sl. | Technical Specification Clause no. | Description | Pre-Bid Queries | POWERGRID Comments/ Clarifications |  |  |
| 1 | BOM/ TS rev no. 09 Clause 20.1/Scope of work point no. 1 | Reactor Protection - Differential Protection Relay | Request to provide the quantity breakup for differential protection relays required for Reactors and ICT | Attached herewith as Annexure-I. |  |  |
| 2 | BOM/ TS rev no. 09 Clause 20.1/ Scope of work point no. 1 | Reactor Protection - Differential Protection Relay | In case relay required for ICT, then please share the number of windings/line ends | Relays to cater functionality for 3-windings. |  |  |
| 3 | BOM/ TS rev no. 09 Clause 20.2/ Scope of work point no. 1 | Reactor Protection - Restricted Earth Fault Protection Relay | Can the desired function be achieved by using 2 relays (1 numerical relay for REF + 1 numerical relay for over fluxing function) without compromising on specs ? | Yes. However their combined pricing shall be evaluated against this Line Item. Further it may be taken note that there might be space constraint in the existing relay panels in case two relays are provided as proposed depending upon the relay sizes that are being offered. Any space constraint shall be taken care by the Contractor (by means of new panel/ Relay shifting etc.) without any additional financial implication to POWERGRID in this regard. |  |  |
| 4 | BOM | Voltage Levels for all sites | Kindly provide voltage levels for all 8 sites mentioned in BOM | Pithoragarh and Sitarganj S/S have 220/132kV Level. Rest all requirements are from 400/220kV Level. |  |  |
| 5 | Scope of Work | Relays to be replaced | Kindly share the details of the existing relays to replace on site . | Attached herewith as Annexure-I. |  |  |
| 6 | 06-Annexure - C (BDS) Make in India | Preference for Local Content more than 60% | As per circular of DIPP , P-45021/2/2017-PP(BE-II) dated 28.05.2027 , There are no item defined for relays in table incorporated in this circular for local content . Request to clarify whether relays as an item is covered separately in DIPP . Whether local content clause will be applicable for relays ? | Minimum Local Content‘ which is 60% for FY2018-19 and 75% over next five years in phased manner mentioned against S.No 13 at Table 3.0 of MoP Order dated 20.12.2018. |  |  |
| 7 | 05-Annexure - B (BDS) eRA | Reverse Auction | Kindly confirm whether RA is applicable for this tender ? | As per ITB 29.1, Supplemented in BDS, e-RA is applicable for the subject Package. |  |  |
| 8 | General | Retrofit Schedule | There is no Retrofit Schedule and time line is indicated after delivery of relays . Request to indicate estimated timeline for Retrofit of relays . | Delivery schedule provided in bidding documents pertains to overall supply and service portions. All Retrofit works to be completed within this delivery schedule. |  |  |