Clarification-I to the bidding document for the Shifting/modification of 400 kV,765 kV HVAC & 800 kV HVDC transmission lines within ROW of "Bundelkhand Expressway" constructed by UPEIDA; Spec Number: 5002001211/OTHERS/DOM/K00 - NR3 RHQ -1

| Para No | Query | Reply |
| --- | --- | --- |
| 1 | As per RFX BOQ Sr. No. 37& 38 against 765 KV S/C AGRA-FTP-II & 765 KV S/C AGRA-FTP-I Tr. Lines (With Bersimis conductor) the required Insulators are 160kN for Suspension & 210kN, While in Technical Specification Section-I, Page No. 24 of 47 it is mentioned that 120kN & 210KN Insulator will be use | Rates may be quoted considering provisions of Technical Specification i.e. 120 KN & 210 KN for 765kV Single Circuit and 160 KN & 210 KN for 765kV Double Circuit lines. Please refer Amendment No –I to the bidding document. |
| 2 | As per RFX BOQ Sr. No. 40 against +800 KV CHAMPA – KURKSHETRA Tr. Line, the required Insulator is 800KV-210KN-DMR Composite long rod Insulators. In this regards we understand that, it should be 132kV -210KN DMR instead of 800kV | Provisions of the bidding documents shall prevail. |
| 3 | As per RFX BOQ Sr. No. 58, there is as requirement of Single Suspension String 132kV AC Twin Lapwing Conductor. We understand that for this Hardware fitting, 160kN DMR Insulator will be used. However, the quantity & Specification for composite insulator for 132kV 160kN DMR is not available. | Provisions of the bidding documents shall prevail. |
| 4 (A) (i) | TOWER PARTS, BOLTS & NUTS: Kindly confirm the dismantling of tower is to be done as manually i.e. piece wise dismantling or to cut from stub level with the help of gas cutter. Also confirm full stub has to be dismantled by braking concrete till base or stub to be cut up to ground level. | 4 (A) (i) (a) Tower materials shall be dismantled piece wise, transported to store and stacked mark No wise as directed by Engineer-In-Charge. 4 (A) (i) (b) The stub to be dismantled to make field good for use/ ploughing. 4(A)(i) (c) A joint verification shall be made with POWERGRID official before dismantling of all the material i.e. tower, hardware fittings, accessories, conductor, insulators & earthwire etc. Handing over shall be as per the said inspection report. |
| 4 (A) (ii) | TOWER PARTS, BOLTS & NUTS: Dismantled towers are to be returned in scope condition or in usable condition. Whether dismantled tower has to be stacked mark number wise in PGCIL store | Please refer reply at 4 (A) (i) (a) above. |
| 4 (A) (iii) | TOWER PARTS, BOLTS & NUTS: Dismantled material’s segregation and staking at PGCIL Store in whose scope | Please refer reply at 4 (A) (i) (a) above. |
| 4 (A) (iv) | TOWER PARTS, BOLTS & NUTS: Dismantled Bolt Nuts cannot be return as per BOM weight as there are chances of misplaced during dismanteling work. | Please refer reply at 4 (A) (i) (a) above. |
| 4 (B) (i) | CONDUCTOR: Whether dismantled conductor has to be re-winded in drum and to be returned in good usable condition or it has to be returned in scrap condition i.e bits of random length. | 4 (B) (i) Material dismantled to be returned in good condition/ as exists in the line. |
| 4 (B) (ii) | CONDUCTOR: What percentage will be considered towards conduction erosion to work out unit weight of dismantled conductor. | 0%. |
| 4 (C)(i) | EARTHWIRE: Whether dismantled earth-wire /OPGW has to be re-winded in drum and to be returned in good usable condition or it has to be returned in scrap condition i.e bits of random length. | Please refer reply at 4 (B) (i) above. |
| 4(D)(i) | INSULATOR: Long rod/Disc/polymer insulator must have been used in existing line, while dismantling some of the insulators/Grading rings may get damaged/ misplaced. Whether damaged insulator/grading ring will be considered as accepted while returning. | Please refer reply at 4 (B) (i) above. |
| 4(E)(i) | LINE HARDWARE FITTINGS: It might happen, that corona ring, arcing horn, bolts & nuts are missing in existing line hardware fittings, also while dismantling some of the items may get misplaced so whether dismantled material i.e hardware has to be returned in scrap condition on weight basis. | Please refer reply at 4 (B) (i) above. |
| 5. | The type test clause indicates material should have been type tested within the last 5 years of tender opening. Please note that in recent years, PGCIL have removed this 5 years validity clause for Type tests as long as there is no change in manufacturing location and design. Looking at the above and also the project size, request your good self to remove the time period clause of 5 years for type tests of all products i.e. Conductor, Insulators, OPGW, Eathwire, Hardware & Accessories etc | Provisions of the bidding documents shall prevail. |