| Sr.No | Clause No./sections | Existing Clause in the Bidding Documents | Amended as |
| --- | --- | --- | --- |

| 1 | BPS PRICE Sch-1 and Sch-2 | S.N.; ACTIVITY DESCRIPTION; MATERIAL CODE; DESCRIPTION; UNIT; QTY. 21; Fabrication and Supply; 1000075363; FABRICATION, GALVANISING AND SUPPLY OF STUBS & CLEATS FOR VARIOUS TYPEOF TOWERS, TOWER EXTENSIONS (COMPLETE) MADE UP OF STEEL GRADE C WITH PACK WASHERS,INCLUDING BOLTS & NUTSFOR 220KV D/C (ACSR DEER) NARROW BASE TOWERS (WZ5) DESIGNED IS 802-2015 FOR HILLY TERRAIN (ALTITUDE 5400 METER)); TOWER TYPE DD45 (UP TO +9M EXTENSION); EA; 9. 22; Fabrication and Supply; 1000075362; FABRICATION, GALVANISING AND SUPPLY OF STUBS & CLEATS FOR VARIOUS TYPEOF TOWERS, TOWER EXTENSIONS (COMPLETE) MADE UP OF STEEL GRADE C WITH PACK WASHERS,INCLUDING BOLTS & NUTSFOR 220KV D/C (ACSR DEER) NARROW BASE TOWERS (WZ5) DESIGNED IS 802-2015 FOR HILLY TERRAIN (ALTITUDE 5400 METER)); TOWER TYPE DD45 (FOR +18/25M EXTENSION); EA; 6. | S.N.; ACTIVITY DESCRIPTION; MATERIAL CODE; DESCRIPTION; UNIT; QTY. 21; Fabrication and Supply; 1000075363; FABRICATION, GALVANISING AND SUPPLY OF STUBS & CLEATS FOR VARIOUS TYPEOF TOWERS, TOWER EXTENSIONS (COMPLETE) MADE UP OF STEEL GRADE C WITH PACK WASHERS,INCLUDING BOLTS & NUTSFOR 220KV D/C (ACSR DEER) NARROW BASE TOWERS (WZ5) DESIGNED IS 802-2015 FOR HILLY TERRAIN (ALTITUDE 5400 METER)); TOWER TYPE DD (UP TO +9M EXTENSION); EA; 9. 22; Fabrication and Supply; 1000075362; FABRICATION, GALVANISING AND SUPPLY OF STUBS & CLEATS FOR VARIOUS TYPEOF TOWERS, TOWER EXTENSIONS (COMPLETE) MADE UP OF STEEL GRADE C WITH PACK WASHERS,INCLUDING BOLTS & NUTSFOR 220KV D/C (ACSR DEER) NARROW BASE TOWERS (WZ5) DESIGNED IS 802-2015 FOR HILLY TERRAIN (ALTITUDE 5400 METER)); TOWER TYPE DD (FOR +18/25M EXTENSION); EA; 6. |
| --- | --- | --- | --- |
| 2 | Clause 2.7.5, Section-IA of Technical Specification TL02 | Sag Tension Condition Sr no.; Temp (0C); Wind Factor; Radial Ice thk(mm); Remarks. --; --; --; --; --. 8; -15; 0.25; 0; Loading Cond-ice shedding^. --; --; --; --; --. # For security conditions under reduced wind and full ice, 25% of full wind pressure shall be considered. ^ Ice shedding condition: 200 m span with 15 mm radial ice on one side and 100m span with no ice on other side at -15 degree C and 25% of full wind. $ Mid-span clearance for Ruling --------- --------- at cl. 1.4.10 (i) of Sec- IV A. | Sag Tension Condition Sr no.; Temp (0C); Wind Factor; Radial Ice thk(mm); Remarks. --; --; --; --; --. 8; -15; 0.25; 0; Loading Cond-ice shedding^. --; --; --; --; --. ^ Ice shedding condition: - 200 m span with 15 mm radial ice on one side and 100m span with no ice on other side at -15 degree C and 25% of full wind. - Tension at -15 degree C and 25% of full wind & no ice for 100m span is to be arrived by considering INITIAL CONDITIONS as given below – Temp (0C); Wind Factor; Radial Ice thk(mm); Tension. -30; 0; 0; Tension value obtained for 200m span at -30 deg, nil wind and no ice condition. $ Mid-span clearance for Ruling ----------- ----------- at cl. 1.4.10 (i) of Sec- IV A. |
| 3 | Clause 2.14.2, Section-IA of Technical Specification TL02 | Guaranteed technical particulars of ACSR DEER conductor ………………….. --; --; --; --. 4.7; Linear mass of the conductor. a); -----. b); ----. c); Maximum; Kg/km; 2019. Other provisions as mentioned in Section VIIA shall remain unchanged. | Guaranteed technical particulars of ACSR DEER conductor ………………….. --; --; --; --. 4.7; Linear mass of the conductor. a); -----. b); ----. c); Maximum; Kg/km; 2019. 4.8; Sectional Area of conductor; Sqmm; 529.8. 4.9; Modulus of Elasticity; Kg/Sqmm; 8158. 4.10; Coefficient of linear expansion; Per Deg C; 0.0000178. Other provisions as mentioned in Section VIIA shall remain unchanged. |
| 4 | In view of the above Amendments, the ‘Price_schedule’ excel stand revised as ‘Price_schedule_Rev01’. Note- Bidders are requested to consider the revised excel sheet(s) titled “Price Schedule_Rev01” for bid preparation/submission for the subject package. |  |  |