## TL02
Clarification No- I dated 09/10/2024 to the Bidding Documents for Transmission Line Tower Package- TL02 for 220 kV S/C (on D/C Tower) Pang-Upshi (Part-2) 220kV AC Transmission line between Pang and Phyang associated with Transmission system for evacuation of RE power from renewable energy parks in Leh (5 GW Leh-Kaithal transmission corridor); Spec. No: CC/NT/W-TW/DOM/A06/24/12013
Sl no. | Re. Clause no. | Existing provision | Bidder's Query/Comment | POWERGRID Reply
1 | Clause 1.4.1 TL02 | …............The base width & other dimension of tower shall be finalized by contractor as per the site requirement meeting all required design parameters as stipulated in this technical specification. | Kindly provide base width of narrow based tower | Bidder may refer clause no. 1.4.1 of Sec-1A
2 | Cl.:2.2.1,page :4 & 5 of 25, Sec-1A | 4 types of towers are classified (DA,DB, DC & DD(30-60 deg dev) | In price schedule tower type is mentioned DD ,but stubs are mentioned as DD45. Please confirm the stubs are also for Tower type DD(30-60 deg deviation) only. | Tower as defined in relevant clause is DD/Narrow Base DD, not DD45. For correction in BOQ, refer BOQ amendment No-II
3 | Clause 1.4.1 - TL02 | These narrow base towers shall be designed as one circuit terminated on one cross arm whereas other circuit shall be terminated at body itself . The circuit which is terminated at body shall be routed through jumper with pilot attached at auxiliary cross arm attached at other side. | In Snow zones, the middle conductors should be staggered from the top and bottom conductor, as this staggering helps to mitigate the galloping effect, which can cause mechanical oscillations and potential damage to the power lines. Please clarify. | Bidder may refer provisions of TS.
4 | Technical specification Volume II Section 1A, Clause : 2.14.1 Conductor & OPGW for 220 kV line | Conductor & OPGW for 220 kV line | Cross section area, Modulus of elasticity and coefficient of thermal expansion details are not included. Kindly add details for ACSR DEER conductor. | Bidder may refer Amedment No-II
5 | Technical specification Volume II Section 1A, Clause no 2.2 | Classification of Towers | As per classification tower designs are required for narrow base tower for tower type DB, DC & DD, however base width restriction not included in specification for each type of tower. Kindly provide maximum base width dimension to be considered in design for all tower types. | Bidder may refer clause no. 1.4.1 of Sec-1A
6 | Technical specification Volume II Section 1A, Clause no 2.2 | Classification of Towers | We understood that the design of narrow base towers only included in scope of bidder as provided in price schedule. Design of other normal base towers which are required for the project not included in scope of the bidder and drawings of the normal base towers will be provided by PGCIL. Kindly clarify the same. | Bidder's understanding is correct.
7 | Technical specification Volume II Section 1A, Clause 2.9 | Grillage Foundation | As per specification contractor may adopt grillage type foundation however in price schedule grillage type foundation not included. We understood that, If grillage type foundation required during project execution, PGCIL will provide the foundation design & drawing of the same. Please clarify. | Bidder's understanding is correct.
8 | Technical specification Volume II Section 1A, Clause 2.10 | Avalanche Protection | As specified in specification “The drawings for avalanche protection structure and tower foundation for avalanche protection (raised chimney foundation up to 9.5 m with/ without tie beam) shall be released to the contractor during execution stage”. For towers and foundation designs which included in bidders’ scope, there is no any additional loading consideration or structural provision required due to avalanche protection. Kindly clarify. | Bidder's understanding is correct.
9 | Technical specification Volume II Section 1A, Clause 2.12 | Use of Helicopter/ Helicrane for Transportation of Transmission Line materials from site store to tower location | We understood that Helicopter/Helicrane to be used for material transportation only. Assembly of tower panels to be done at tower location. Lifting of tower panels and tower erection with use of Helicopter/Helicrane not required. Kindly clarify. If lifting of tower panels required for erection purpose with use of Helicopter / Helicrane, kindly provide details of additional loading or additional provisions which are to be consider in tower design/drawing. | Bidder may refer clause no. 2.12 of Section -IA (Vol-II)
10 | General Queries |  | Request you to provide the kmz file for route of all three packages. | Link for the same is shared with this clarification. The shared KMZ file is for reference only. However, Bidders may visit the line route to acquaint themselves with terrain conditions and associated details of the proposed transmission lines.
11 | General Queries |  | Request you to provide Sag Tension Calculations. | The data shall be provided to successful bidder.
12 | General Queries |  | Request you to kindly provide Tower Spotting data. | The data shall be provided to successful bidder.
13 | General Queries |  | Request you to provide the Tower Outline Diagrams for towers which are in PGCIL scope. | Tower outline diagram enclosed in the drawing section of TS Vol-II may be refered.
14 | Technical specification Volume II Section 1A, Clause : 2.14.1 Conductor & OPGW for 220 kV line TL02 | Conductor & OPGW for 220 kV line | For ACSR Deer Conductor, Conductor spacing, Cross sectional area, Modulus of Elasticity and Coefficient of Thermal expansion have not been provided. Please provide the inputs. | Bidder may refer Amedment No -II other than conductor spacing. Transmission line envisaged under the package is single deer conductor. However, for phase to phase clearance, bidder may refer provision of TS/ IS 5613.
15 | General Query |  | Kindly provide the kmz file for the routes | Link for the same is shared with this clarification. The shared KMZ file is for reference only. However, Bidders may visit the line route to acquaint themselves with terrain conditions and associated details of the proposed transmission lines.
16 | Clause 1.4.1 TL02 | It is mentioned that few stretches of the transmission line are passing through very narrow corridor and may require narrow base towers. These narrow base towers shall be designed as one circuit terminated on one cross arm whereas other circuit shall be terminated at body itself. It is further mentioned that the base width & other dimension of tower shall be finalized by contractor as per the site requirement meeting all required design parameters as stipulated in this technical specification. | Kindly provide base width requirement, tower leg slope, available area for foundation at site to be considered for tower design | Bidder may refer clause no. 1.4.1 of Sec-1A
17 | Cl.2.2.1 & 2.7 Sec-1A TL 02 | DD/Narrow Base DD with deviation limit 30-60 degree, whereas as per CL 2.7 deviation limit for Narrow Base DD is not mentioned. Moreover, as per BPS design of DD45 Narrow Base Tower is in scope of bidder. | We understand that we need to design DD45 Narrow Base tower only as mentioned in BPS. Please confirm. | Tower as defined in relevant clause is DD/Narrow Base DD, not DD45. For correction in BOQ, refer BOQ amendment no.-II
18 | Clause 2.7.5 Sec-1A - TL02 | Tension at -15 degree C and 25% of full wind & no ice. Loading condition- Ice shedding condition i.e. 200m span with 25mm radial ice on one side and 100m span with no ice on other side at -15 degree C and 25% of full wind. | We understand that Tension at -15 degree C and 25% of full wind & no ice for 100m span is to be arrived by considering initial condition of -30 deg, nil wind and no ice and tension value obtained for 200m span at -30 deg, nil wind and no ice condition for ice shedding condition. Please confirm | Bidder's understanding is correct. Refer amendment no. -II.
19 | General -TL02 | As per IS 5613(Part 2/Sec 1) Clause no. 7.3, minmum electrical clearance between conductors required 8.4 meter for 220 KV double circuit towers (page 22). | As per IS 5613(Part 2/Sec 1) Clause no. 7.3, minmum electrical clearance between conductors required 8.4 meter for 220 KV double circuit towers (page 22). Please confirm our understanding is correct. | Bidder's understanding is correct.
20 | General- TL02 |  | Horizontal phase clearance requirement not included in specification. Kindly provide minimum horizontal phase to phase clearance requirement for 220 KV. | Bidder may refer provision of TS/ IS 5613